## Introduction
Date: 24 June 2015
Purpose: Publication of TYNDP2016 project candidates for public consultation
Which information is provided in this document?
This document lists all TYNDP2016 project candidates for transmission infrastructure and storage. It is based on applications made by project promoters (individually or jointly) during April 2015, in a process organized by ENTSO-E following the EC's draft guidelines for inclusion of projects in the TYNDP 2016 ("European Commission Guidelines on equal treatment and transparency criteria to be applied by ENTSO-E when developing its TYNDP as set out in Annex III 2(5) of Regulation (EU) No 347/2013"), and supervised by EC, ACER and the Network Developement Stakeholders Group. These projects are proposed for CBA (Cost Benefit Analysis) based assessment in the TYNDP2016 report, starting in October 2016. More background information on investment needs, potential and barriers can be accessed in ENTSO-E's latest Regional Investment Plans which are published at the same time as this draft project list. The reader is invited and advised to form views on this project list together with the regional key messages and study results elaborated in these Regional Investment Plans. This document also lists reference capacities by border that ENTSO-E proposes to use in its CBA assessments by project. For more information on the interpretation of these values, we refer to the CBA methodology as adopted by the EC in February 2015, and the explanation provided in the Regional Investment Plans. We note explicitly that these reference capacities are not to be confused with target capacities or present net transfer capacities. A short explanation is also given below.
Why is this material published for public consultation?
The CBA-based assessement of all TYNDP projects is a very time and resource intensive exercise conducted by ENTSO-E's members. This exercise commences shortly after summer 2015, with preparatory work already underway. In application of the CBA principles, reference assumptions (reference capacities, base case datasets) depend on which projects are, or are not, accounted for (A short explanation is also given below). It is for this reason that a TYDNP project list is consolidated more than a year ahead of the publication date of the final TYNDP report and is consulted to get stakeholders buy-in. In Q2/2015, ENTSO-E also conducted a public consultation on the storyline, data assumptions, methodologies and quantifications (installed capacities and country balances) of various 2020 and 2030 scenarios. ENTSO-E needs views from the wider industry early in the process to ensure the assessment work starts based on data and a project list which is supported and understood. Based on feedback from all interested stakeholders, the project list and reference capacities will be finalized in September 2015.
What is expected from me, and how do my views support the process?
You are invited to express your views via the ENTSO-E consultation platform at https://consultations.entsoe.eu/ by 10 September 2015. ENTSO-E holds a public workshop at the start of the consultation on 24 June, and will continue regular interactions with ACER, EC, the Network Development Stakeholder Group and project promoters. Your views expressed during this consultation, will be taken into consideration when finalizing the project list end of September, and will be a reference for further discussion with the Stakeholder Group, ACER and EC. Also during the assessment phase, ENTSO-E plans to share regular updates on the study progress to ensure early feedback, and maximize understanding among all involved parties.
How is the TYNDP 2016 developed? And in particular, how is the project list established?
The TYNDP 2016 elaboration process is basically split into 2 phases: from Autumn 2014 to Summer 2015; and from Summer 2015 to Autumn 2016. The second phase is basically the systematic CBA assessment of TYNDP 2016 projects against the TYNDP 2016 scenarios and two horizons (2020 and 2030), with publication of the TYNDP 2016 report in consultation in Summer 2016 and finalisation by October. The first phase consisted of parallel processes preparing the second phase: i/ methodologies refinements; ii/ the preparation of all scenarios; iii/ the common regional planning studies exploring the investment needs by 2030 in all 6 concerned regions and identifying candidate grid reinforcements; iv/ the compilation of the TYNDP 2016 project list. The compilation of the TYNDP 2016 project list complies with the EC's draft guidelines for inclusion of projects in the TYNDP 2016 ("European Commission Guidelines on equal treatment and transparency criteria to be applied by ENTSO-E when developing its TYNDP as set out in Annex III 2(5) of Regulation (EU) No 347/2013") and applies to all project promoters, hence equally both to ENTSO-E and non ENTSO-E members. It consists of: an application window, opened to all project promoters in April 2015; a review of all project application by ENTSO-E, ensuring applications are complete, in May 2015; a consultation about the draft TYNDP 2016 project list during the Summer 2015; a validation of the final project list by ENTSO-E by October 2015, accounting for the feedback received in the consultation. The Network Development Stakeholders Group reviewed the principles of this process in February 2015 and proposed to act as an ethical committee to the process. In this respect, they received reports about the received applications by ENTSO-E early May, and debated early June about the inclusion of projects not meeting all criteria. They will also receive the feedback from the consultation mid September and make recommendations about the inclusion or not of some applications today "as yet incomplete". (EC and ACER are represented at the Network Development Stakeholders Group.)
On which basis are candidate projects for CBA assessment and publication in the TYNDP 2016 accepted?
Criteria for project selection in the TYNDP 2016 are depicted in the EC's draft guidelines for inclusion of projects in the TYNDP 2016 ("European Commission Guidelines on equal treatment and transparency criteria to be applied by ENTSO-E when developing its TYNDP as set out in Annex III 2(5) of Regulation (EU) No 347/2013"). Minimum technical standards are set out for the projects, in order to ensure they match concerns of European relevance. In order not to bias the assessment process of other projects, every project promoter must also provide documentation demonstrating their ability to actually conduct the project and especially the support of relevant Authorities. During the application window of April 2015, some requests were made for which at this point it cannot yet be proven that the application complies with the legal and technical criteria provided in the EC's guidelines. The Network Development Stakeholder Group, acting as ethical committee to the process debated these issues in a web conference on 10 June 2015. They acknowledge that i/ strict rules must be obeyed to ensure a serious and fair assessment; and ii/ formally, projects not matching the rules are not included in the present project list, but are mentioned separately as applications "not yet complete"; however iii/ EC's guidelines are still to be formally adopted; iv/ with late information, project promoters may have had difficulties to supply all the requested information ; v/ as long as the missing information, or equivalent, is provided by September, the project application will be reviewed by the Network Development Stakeholder Group in September and possibly recommended to be part of the final list, provided that there are only a limited number of cases and no other project assessment is influenced (as a consequence, the project will be assessed always with the PINT approach). Hence, depending on the outcome of the consulation, and further documentation provided by the promoter during this period, these may still be included in the final project list taking into account views of the Network Development Stakeholder Group.
How do the reference capacities and classification of projects relate?
A new aspect in the TYNDP2016's project list is the classification into mid-term, long term and future projects. This classification responds to earlier requests from ACER and stakeholders to have three main sets of investments in a TYNDP depending on commissioning date and maturity of the projects. This has also a strong link with the reference architecture on which a project is assessed with the CBA methodology. The methodology provides for a Take-Out-One-at-a-Time approach - TOOT - (by which a project is assessed by checking the impact of taking it out of the reference), or a Put-IN-one-at-a-Time approach - PINT - (assessed by putting it in). The three categories proposed in this list are: - Mid-term projects: are projects to be commissioned by 2022 and acknowledged in the latest national plans or having intergovernmental agreement - these will be assessed by TOOT method against the expected 2020 network, and against the expected 2030 network. - Long-term projects: are projects to be commissioned by 2030 and acknowledged in the latest national plans or having intergovernmental agreement - these will be assessed by PINT method against the expected 2020 network, and by TOOT method against the expected 2030 network. - Future projects: cover all other projects which do not fall under the previous categories - these will be assessed with PINT method against the expected 2030 network. The expected 2020 and 2030 network results in reference cross-border capacity assumptions for network studies (and later on, datasets for grid studies), and mainly cover the present grid and projects covered in national plans and intergovernmental agreements. In other words, the 2020 expected network covers mid-term projects; the 2030 expected network covers mid-term and long-term projects. Note that 'future projects' are assessed via PINT (i.e. on top) of the reference grid, and are thus not part of the reference capacities. As such each TOOT assessed project impacts the others; while a PINT assessed project does not directly impact another project's assessment.
Any further questions?
For any further questions about this consultation or suggestions on the entire TYNDP process, please contact consultations@entsoe.eu, or join our workshops and webinars. We appreciate to hear your views.

## TYNDP2016 transmission
Boundary | Project candidate name | Description | Provisional GTC [MW] | TYNDP2014 reference (if applicable) or motivation for new project candidates | Detailed studies | Expected Commissioning Year | Classification | Project promoter(s)
Austria - Germany | St. Peter - Pleinting | ​Increase of the cross border transmission capacity by erecting a new 380kV line between St. Peter (Austria) and Pleinting (Germany). This leads to an improved connection of the very high amount of RES in Germany and the pump storages in the Austrian Alps. | 1500 | 187 | new 380-kV-line Pleinting (DE) - St. Peter (AT) on existing OHL corridor | 2022 | Long-term Project | APG;TENNET-DE
Austria - Italy | Wurmlach (AT) - Somplago (IT) Interconnection | " Somplago - Wurmlach interconnection is a third party cross-border electrical line promoted by Alpe Adria Energia SpA​. The project concerns a 220kV a.c. merchant line, 300 MVA from Somplagosubstation to Wurmlach substation, including a 300MW Phase Shift​ Transformer, located in Austria ." | 275 | 210 | (tbc) | 2018 | Mid-term project | Alpe Adria Energia SpA
Austria - Italy | Austria - Italy | Reinforcement of the interconnection between Italy and Austria via two new single circuit crossborder lines and closure of the 380-kV-Security Ring in Austria. | Direction A: 1100 - Direction B: 1000 | 26 | The project supports the interaction between the RES in Italy and the eastern part of Austria with the pump storage power plants in the Austrian Alps. | 2023 | Long-term Project | APG;TERNA
Belgium - Germany | 2nd interconnector Belgium - Germany | This project considers the possibility of a second 1 GW HVDC interconnection between Belgium and Germany. The determination of the optimal capacity, location, technology, potentially needed internal grid reinforcements and possible synergies on the integration of this interconnector in relation to the long-term concept of a west-east corridor are subject of further studies.. | 1000 | 225 | This is a conceptual project that could be considered as a long-term investment option, where preliminary analysis has shown the potential for further market integration triggered by high-RES scenarios. | 2030 | Future Project | AMPRION;ELIA
Belgium - Germany | ALEGrO | This project involves the realization of a HVDC link with a bidirectional rated power of approximately 1.000 MW capacity, as the first interconnection between Belgium (Lixhe) and Germany (Oberzier). Internal reinforcements in AC grid in Belgium are amongst others needed to facilitate the integration of ALEGrO - creation of 380kV substation at Lixhe, including a 380/150kV transformer - creation of 380kV substation in Genk (André Dumont), including a 380/150 kV transformer - addition of a second circuit on line Lixhe-Herderen Additional potential reinforcements in the AC grid in Belgium are subject to monitoring the potential for new production units at Lixhe - creation of a second line between Lixhe & Herderen - installation of a second 380/150kV transformer in the Limburg area (substation André Dumont is reference) | 1000 | 92 | First of all, ALEGrO enhances the internal market integration by enabling direct power exchanges between these countries Secondly, the new interconnection will play a major role for the transition to a generation mix which is undergoing structural changes in the region (high penetration of RES, nuclear phase-out, commissioning and decommissioning of conventional power plants etc.). Given these major changes in the production mix, the new interconnection also contributes to the security of supply in facing the arising challenges for secure system operation. | 2020 | Mid-term Project | AMPRION;ELIA
Belgium - Great Britain | Thames Estuary Cluster (NEMO) | ​This projects envisions the realization of NEMO - the first interconnector between Great Britain and Belgium – as a 1 GW HVDC link with technical commissioning by 2018 and commercial operation in 2019, including a number of onshore UK reinforcements to facilitate this and other potential interconnector connections within the Thames Estuary region. | 1000 | 74 | NEMO enhances market integration, facilitates the penetration of renewable energy sources in the energy mix and contributes to security of supply since providing import capacity in a context of decommissioning of power plants. | 2018 | Mid-term Project | ELIA;NGT
Belgium - Great Britain | 2nd interconncetor Belgium - UK | This project considers the possibility of a second 1GW HVDC connection, between UK (Kemsley) and a Belgian 380kV substation in the Antwerp area (Doel, Zandvliet are indicative locations). The determination of the optimal capacity, location, technology, potentially needed internal grid reinforcements and possible synergies on the integration of this interconnector in relation to an offshore hub/grid or the concept of a "west-east corridor" are subject of further studies. | 1000 | 121 | This is a conceptual project that could be considered as a long-term investment option, where preliminary analysis has shown the potential for further market integration triggered by high-RES scenarios. | 2030 | Future Project | ELIA;NGT
Belgium - Netherlands | Belgium-Netherlands: further evolution | A bilateral study is started to investigate the options for developing additional cross-border capacity between Belgium and The Netherlands (1000 MW), in addition to existing and planned projects. The reference solution envisions the reinforcement of the cross-border lines Zandvliet(BE)-Kreekrak(NL) and/or Van Eyck(BE)-Maasbracht(NL) with high performance conductors combined with the installation of additional phase shift transformers. The bilateral study will further evaluate the balancing of flux control measures between both x-border lines, hereby not excluding alternative solutions. | 1000 | A need has been identified to develop additional cross-border capacity between Belgium and The Netherlands, related to the security-of-supply perspective with planned nucleair phase out in Belgium. Market analysis (Common Planning Study) indicate that additional cross-border capacity is also necessary from market integration perspective. The timing of 2025 is indicative and the bilateral study will furhter evaluate the possibilities envisioning a shorter-term horizon. | ​Common Planning Studies & Internal Studies | 2025 | Future Project | Elia System Operator;TenneT TSO
Bulgaria - Greece | Third interconnector between Bulgaria and Greece | ​The new project concerns the construction of a new 400kV overhead line between the substations Nea Santa (GR)-Maritsa East 1 (BG). | 500 | The project necessity stems from the need to increase the transfer capacity between Greece and Bulgaria in order to accomodate connection of RES and improve market integration, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. |  | 2030 | Future Project | IPTO;ESO EAD
Bulgaria - Serbia | New double 400 kV interconnection line between Bulgaria and Serbia | New double 400 kV interconnection line between Bulgaria and Serbia | 800 | ​Market integration and RES connection | The project necessity stems for the need to increase the transfer capacity between RS and BG in order to accomodate connection of RES and market integration, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4.​ | >2030 | Future Project | ESO EAD;JP EMS
Countries around the Northern Seas | Long term conceptual North Seas Offshore grid infrastructure | Potential synergies to be further studied given the preliminary ideas on a global scheme for offshore infrastructure in the North Seas, complemented with the long term perspective for further market integration as per analysed TYNDP2014 vision 4 scenario. | TBD | ​RES integration and increase the integration level between countries, including necessary onshore reinforcements | Common Planning Studies​ | >2030 | Future Project | EirGrid;Elia System Operator;Energinet.dk.dk;Creos Luxembourg;National Grid;RTE;TenneT TSO GmbH;SONI;Statnett;TenneT TSO
Croatia - Bosnia Herzegovina | Upgrading of existing 220 kV lines between HR and BA to 400 kV lines | ​Upgrading of existing 220 kV lines between SS Đakovo (HR) and SS Tuzla/Gradačac (BA) to 400 kV lines. | 500 | ​The project necessity stems for the need to increase the target transfer capacity between HR and BA in order to accommodate exploitation of RES and market integration, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4. | ​Common Planning Studies​ | 2030 | Long-term Project | HOPS;NOS BiH
Croatia - Serbia | New 400 kV interconnection line between Serbia and Croatia | Construction of new 400 kV interconnection line Sombor (RS) - Ernestinovo (HR) | 500 | ​Market integration and Security of supply | The project necessity stems for the need to increase the transfer capacity between RS and HR in order to accommodate connection of RES and improve market integration, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4.​ | 2030 | Future Project | HOPS;JP EMS
Cyprus - Greece - Israel | EuroAsia Interconnector | The Euro Asia Interconnector consists of a 400 kV DC underwater electric cable and any essential equipment and/or installation for interconnecting the Cypriot, Israeli and the Greek transmission networks (offshore). The Interconnector will have a capacity of 2000 MW and a total length of around 820 nautical miles/around 1518 km (approx. 329 km between CY and IL, 879 km between CY and Crete and 310 km between Crete and Athens) and allow for reverse transmission of electricity | 2000 | 219 | (tbc) | PCI 3.10.1 12/2019, PCI 3.10.2 12/2022, PCI 3.10.3 12/2020 | Mid-term project | EuroAsia Interconnector
Czech - Germany | PST Hradec | ​​Installation of 4 Phasing Shifting Transformers (PSTs) at the substation Hradec on the 400 kV interconnector (double-circuit line) between Hradec on the Czech Republic side and Rohrsdorf on the German side. The 4 PSTs in Hradec, each has rated throughput power of 850 MVA, 2 PSTs units installed in parallel for each tie-line of the double circle line and with a total rated throughput power of 1700 MVA per circuit, with a phase angle of up to 30° and 65 possible settings (-32,...0,...+32) for a rated voltage of 420 kV. | 0-500 | 177 | Installation of PSTs in Hradec at the cross-border interconnection CEPS-50Hertz will enable CEPS to deal effectively with the unplanned cross-border flows at the Rohrsdorf (Germany) - Hradec (Czech Republic) interconnector on both directions and therefore ensure the security of the Czech transmission grid including neighboring grids from a mid-term and a long-term perspective. PSTs will guarantee a very high degree of flexibility and ensure secure operation of the adjacent infrastructure, while keeping the cross-border flows within safe limits. | 2016 | Mid-term Project | CEPS
Czech - Germany | CZ Northwest-South corridor | ​A corridor of internal 400 kV overhead lines inside the Czech Republic connecting new 420 kV substations between Vernerov, Vitkov and existing substation Prestice in the northwest-south direction incuding looping of existing 400 kV overheadline (V413: Reporyje-Prosenice) into the existing substation 420 kV Mirovka. The project consists of building of two new 420 kV substations Vernerov and Vitkov, building of two 400 kV overhead lines involving changing a 220 kV double-circuit lines to 400 kV double-circuit lines with a capacity of 2x1730 MVA between Vernerov-Vitkov and Vitkov-Prestice and building a new double-circuit overhead line between Mirovka and V413. | 0-500 | 200 | The project will increase the transmission capacity in the western part of the Czech grid and therefore enabling the accomodation of the prevailing power flows in the north-west and west-east direction for the entire Central Eastern Europe. Further the project will enable connection of Renewable Energy Sources in the Karlovary region, reduce infrastructure vulnerability and ensure security of supply in the western region of the Czech Republic | 2022 | Mid-term Project | CEPS
Czech - Germany | CZ Southwest-east corridor | A corridor of internal 400 kV overhead lines inside the Czech Republic connecting existing 420 kV substations between Prestice, Kocin, Mirovka and Cebin in the southwest-east direction. The project consists of buidling a new ​AC 400 kV overhead line which connects 420 kV substations Kocin and Mirovka with double circuit line of about 120.5 km lenght and a capacity of 2x1730 MVA, building of a 400 kV overhead lines that involves changing of a 400 kV existing single-ciruit line to double-circuit line with a capacity of​2x1730 MVA between Kocin-Prestice and Mirovka-Cebin. The upgrading of the existing 420 kV substation Kocin is also a part of the project. | 0-500 | 35 | Facilitation of the power flow in the north-south-west-east direction, reducing of infrastructure vulnerability in the southwest-east direction inside the Czech grid, insuring security of supply in the southern regions and provision of additional transmission capacity for connection of potential power generation capacities in the region is the main motivation of this project. | 2028 | Long-term Project | CEPS
Denmark- West - Great Britain | Viking DKW-GB | This project, known as Viking Link and under development by National Grid Interconnector Holdings Limited and Energinet.dk, investigates a 600-700 km connection between Denmark West and Great Britain by two parallel HVDC subsea cables and related substations on both ends. | 1400 | 167 | The project adds cross-border transmission capacity between both countries, thereby facilitating integration of the energy markets and the incorporation of more RES, as the wind is not correlated between both markets. | 2020 | Mid-term Project | Energinet.dk;NGT
Denmark-East - Germany | Kontek-3 | ​The third HVDC connector between Denmark-East and Germany | 600 | ​Market integration, RES connection | Common Planning Studies 2015, with the preliminary market transport capacity 1000 MW (additional).​ | >2030 | Future Project | 50Hertz Transmission;Energinet.dk.dk
Denmark-East - Germany | Kriegers Flak CGS | The Combined Grid Solution (CGS) is new a DC offshore connection between Denmark and Germany. The project is a combined grid connection of the offshore wind farms Kriegers Flak, Baltic 1 and 2 and an interconnection between both countries. | 400 | 36 | The project facilitates RES connection and increased cross border trade of electricity (market integration). | 2018 | Mid-term Project | 50HERTZ;Energinet.dk
Denmark-East - Germany | DKE - DE | ​This project includes a HVDC subsea interconnector between Denmark-East (DKE) and Germany (DE) and is called Kontek-2. A final grid-connection solution is not prepared yet; one of the possible alternatives could establish the Danish HVDC converter station in the area of Lolland- Falster. This alternative comprises among other things an HVDC converter station being connected to the existing 400 kV substation Bjæverskov via 400 kV underground cables and/or 400 kV OHL. | 600 | 179 | The purpose of the project is to further integrate markets and renewables in both countries. | 2030 | Future Project | 50HERTZ;Energinet.dk
Denmark-East - Poland | DKE-PL-1 | The first HVDC connector between Denmark-East and Poland | 600 | ​Market integration, RES connection | Common Planning Studies 2015 with the preliminary market transport capacity of 500 MW (additional).​ | >2030 | Future Project | Energinet.dk.dk
Denmark-West - Denmark-East | Great Belt II | ​This project candidate includes an HVDC connector between Denmark-West (DKW) and Denmark-East (DKE). The connector is called Great Belt-2. It could among other variants be located between the 400 kV substation Malling in DKW and the reconstructed 400 kV substation Kyndby in DKE. | 600 | 175 | The main purpose of this project is to incorporate more RES into the Danish system by sharing reserves between both systems and improve market integration. | 2030 | Future Project | Energinet.dk
Denmark-West - Germany | DKW-DE, Westcoast | ​The project consists of a new 400 kV line from Endrup (Denmark) to Niebüll (Germany), adding more transfer capacity at the West Coast between these countries. On the Danish side, this project includes the establishment a 400 kV AC underground cable system from the existing 400 kV substation Endrup to the border, from where the interconnector continues to Niebüll. The project is labelled by the EC as project of common interest (PCI 1.3.1). | 500 | 183 | The project helps to integrate RES and to strenghten the connection between the Scandinavian and Continental market. | 2022 | Mid-term Project | Energinet.dk;TENNET-DE
Denmark-West - Germany | DKW-DE, step 3 | This project is the third phase in the Danish-German agreement to upgrade the transfer capacity between Denmark West and Germany. The third-phase project consists of a new 400 kV line from Kassoe (Denmark) to Audorf (Germany). It mainly follows the trace of an existing 220 kV line, which will be substituted by the higher voltage line. The project is labelled by the EC as project of common interest (PCI 1.4.1). | Direction A: 720 - Direction B: 1000 | 39 | The project helps to integrate RES and to strenghten the connection between the Scandinavian and Continental market. | 2020 | Mid-term Project | Energinet.dk;TENNET-DE
Denmark-West - Netherlands | COBRA cable | ​'The project is an interconnection between Endrup (Denmark) and Eemshaven (The Netherlands). The project consists of a 320 kV DC subsea cable and related substations on both ends, 320-350 km apart, applying VSC DC technology. The project is supported by the European Energy Programme for Recovery (EEPR) and is labelled by the EC as project of common interest (PCI 1.5). | 700 | 71 | The purpose is to incorporate more renewable energy into both the Dutch and the Danish power systems and to improve the security of supply. Moreover, the cable will help to intensify competition on the northwest European electricity markets. | 2019 | Mid-term Project | Energinet.dk;TENNET-NL
Denmark-West - Netherlands | COBRA-2 | ​The second HVDC connector between Denmark-West and The Netherlands. | 700 | ​Market integration, RES connection | Common Planning Studies 2015 ​with the preliminary market transport capacity 1000 MW (additional). | >2030 | Future Project | Energinet.dk.dk;TenneT TSO
Denmark-West - Sweden (SE3) | Kontiskan 2 | ​Renewal of the existing Kontiskan 2 HVDC connectors between Denmark-West and Sweden (Bidding area SE3), approximately 380 MW, to maintain capacity between Sweden and Denmark. Final capcity to be determined later. | 0 | ​Maintaining existing capacity to ensure a good Market integration and Security of Supply.There are two options: Renewal without increase of capacity or no renewal at all which would mean a decrease from current level. | Bilateral and national socio-economic and technical studies.​ | 2030 | Future Project | Energinet.dk.dk;Svenska Kraftnät
East-West | Aragón-Catalonia south | This project is a reinforcement between Aragón and Cataluña required to solve the congestion on the existing grid, due to unbalanced production and consumption between Aragón and Cataluña, mainly between Teruel and Tarragona. The project consists of a new 400 kV double circuit OHL line between Escatrón and La Secuita ( Spain), and includes new substations in Els Aubals (with direct connection of wind power) and in La Secuita (400/220 kV). ​ | Direction A: 0-30 - Direction B: 0-500 | 157 | market and RES integration, constraints solution | 2027 | Future Project | REE
East-West | Mid Continental East corridor | ​The project consists of one double circuit 400 kV line between Serbia and Romania and reinforcement of the network along the western border in Romania: one new simple circuit 400 kV line from Portile de Fier to Resita and upgrade from 220 kV double circuit to 400 kV double circuit of the axis between Resita and Arad, including upgrade to 400 kV of three substations along this path. The project aims at enhancing the transmission capacity along the East-West corridor in south-eastern and central Europe. It will provide access to the market for more than 1000 MW installed new wind generation in Banat area (Serbia and Romania). | Direction A: 737 - Direction B: 453 | 144 | The project enhances the transmission capacity along the East-West corridor in the South-Eastern and Central Europe. | 2022 | Mid-term Project | TRANSELECTRICA; EMS
East-West | East Coast Cluster | A very high level indication of the works required for GB East Coast. In detail the projects will consist of multiple offshore HVDC and AC circuits and connecting platforms joining to multiple onshore connection points with their own reinforcement requirements. ​ | 3000 | 86 | A very high level indication of the works required for GB East Coast. In detail the projects will consist of multiple offshore HVDC and AC circuits and connecting platforms joining to multiple onshore connection points with their own reinforcement requirements. | 2026 | Future Project | NGT
East-West | CSE8 Transbalkan Corridor | ​The project aim is to increase transmission capacity and facilitate exchange of energy between north-east part of Europe and south-west of Europe. | 1095 | 146 |  |  | Mid-term Project | CGES;EMS;NOS-BIH
Estonia - Latvia | Estonia-Latvia 3rd IC | ​​​​​​Project nr 62 is a planned third 330 kV interconnection between Estonia and Latvia. The project consists of 2 investments of which nr 386 is the main inter-area investment, AC 330 kV OHL between Kilingi-Nõmme substation in Estonia and TEC2 substation in Latvia. Estonia-Latvia third interconnection associated investment nr 735 AC 330 kV OHL Harku-Lihula-Sindi in Estonian. It increases the capacity between Estonia and Latvia by 600 MW. The project also helps to improve SoS and contributes to RES increase in the Baltics western coastal areas. The project is also a precondition for construction of off-shore wind parks in Estonia and Latvia. The Estonia-Latvia third interconnection is the significant project for all the Baltic region, because it will increase competition for electricity market in Baltic States and between Baltic States and Nordic countries. It will provide reliable transmission network corridor will improve interoperability between Baltic states. In addition after commissioning the projects forming the Baltic Energy Interconnection Plan the reinforced Baltic States transmission system and its connections to Nordic and Central Europe can also serve as an alternative route for exporting Nordic surplus to the Central European power system. ​ | 450-600 | 62 | Main objectives are market integration and increase of SoS. | 2020 | Mid-term Project | AST;ELERING
Baltics - Continental Europe | Baltics synchro with CE | This is unique project as main driver for it is not to increase GTC but to disconnect from Russia system and connect with Continental European networks synchronously. Two different landing points and two differently routed interconnections are required to achieve physical separation of the two redundant interconnections in order to establish a reliable synchronous connection between the transmission systems of Baltic States and Continental Europe networks. The first Lithuania – Poland connection (LitPol Link) is already decided and it will be the first connection. The pre-feasibility study of second PL-LT line indicates significant risks, not allowing the effective implementation on PL territory. The list of investments provided during TYNDP2014 process was not final and including just a few of probable necessary investments. Some more investments will be transfered from another project 163 Baltic Corridor which will be not re-confirmed for TYNDP2016 but has identified investement needs that will be necessary for Baltic synchronisation project as well. This is PCI project. Additionally to previously mentioned investments also some new investments will be added in future development of the project, that were discovered during the planning process and will be determined and specified during ongoing studies. | 0-600 | 170 | Project is aimed at infrastructure development for deeper market integration and synchronous operation of the power systems of the Baltic States with the Continental European networks and will increase security of supply for Baltic systems (Estonia, Latvia, Lithaunia). | 2025 | Future Project | AST;ELERING;LITGRID
Finland - Sweden | 3rd AC Finland-Sweden north | ​Third AC 400 kV overhead line interconnector between Finland north and Sweden SE1. Strengthening the AC connection between Finland and Sweden is necessary due to new wind power generation. larger conventional units and decomissioning of the existing 220 kV interconnector. | Direction A: 500 - Direction B: 800 | 111 | Security of supply: The project enhances system security of whole Finnish system, especially during outages on other interconnections between the countries. RES integration: The project helps integrating 500-800 MW wind power in Northern Sweden and Finland and improves the possibilities of balancing the system. | 2025 | Long-term Project | FINGRID;SVK
Finland North-South | N-S Finland (P1) stage 1 | ​Several 400 kV lines are planned in Finland to increase North-South transmission capacity, thus enabling the integration of new renewable and conventional generation in northern Finland and to compensate the dismantling of obsolescent existing 220 kV lines. Stage 1 includes investments up until 2016 | 700-1400 | 64 | Several 400 kV lines are planned in Finland to increase North-South transmission capacity, thus enabling the integration of new renewable and conventional generation in northern Finland and to compensate the dismantling of obsolescent existing 220 kV lines. The commissioninf of the lines is scheduled to take place in segments both in mid and long term. Stage 1 includes the investments up until 2016. | 2016 | Mid-term Project | FINGRID
Finland North-South | Keminmaa-Pyhänselkä | ​The project is 400 kV overhead line in North Finland. Integration of new generation at Bothnian bay and increased transmisison capacity demand. Will help utilizing the Swedis/Finnish cross border capacity. | 500-1000 | 96 | The project is 400 kV overhead line in North Finland. Integration of new generation at Bothnian bay and increased transmisison capacity demand. Will help utilizing the Swedis/Finnish cross border capacity. | 2024 | Long-term Project | FINGRID
Finland North-South | N-S Finland P1 stage 2 | ​Several 400 kV AC lines are planned in Finland to be built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland and to compensate dismantling of obsolescent existing 220 kV lines. This project is 400 kV overhead line from connecting North Finland to South. | 1000 | 197 | Several 400 kV AC lines are planned in Finland to be built to increase the North-South transmission capacity thus enabling the integration of new renewable and conventional generation in northern Finland and to compensate dismantling of the obsolescent existing 220 kV lines. The commissioning of the lines is scheduled to take place in segments both in mid and long term. This project is 400 kV overhead line from connecting North Finland to South. | 2023 | Long-term Project | FINGRID
Finland-Sweden (SE3) | Fenno-Skan 1 renewal | ​​Renewal of the existing 400 kV HVDC cable interconnection between Finland and Sweden. The projects capacity is estimated to range between 500-800 MW which could mean an updgrade compared to today. There are three options: a) renewal with an increase from current level (+300MW) b) no additional capacity (0MW) or c) no renewal at all (-500MW). | 300 | ​Renewal needed due to time and age of the existing equipment.Existing link has been commissioned 1989 and will be ca 40 years old in 2030. |  | 2030 | Future Project | Fingrid;Svenska Kraftnät
France - Belgium | FR-BE phase 2 | ​​​​​​​​​The option that will be evaluated envisions the replacement of the current conductors on the axis Lonny-Achène-Gramme with high performance conductors.The integration of complementary flux control measures is subject to further studies depicting the interaction with the 225kV axis Aubange-Moulaine. Hereby not excluding alternative / complementary solutions (new HVDC corridor, upgrade 225kV to 380kV,...) as per the framework of the long-term concepts of an offshore grid & west-east corridor. | 1000-1400 | 173 | The project aims at sustaining further market integration within the long-term perspective of the energy transition and subsequent need to balance the transit flux between the 225kV and 380kV grids at the east side of the border. | 2030 | Future Project | ELIA;RTE
France - Belgium | France-Belgium Phase 1 | ​The project consists in reconductoring the existing double-circuit 400-kV cross-border line between Lille(Avelin/Mastaing, FR) - Avelgem (BE) - Zomergem (Horta, BE) with High Temperature Low Sag conductors to increase its thermal capacity. | 600-1300 | 23 | The project aims at ensuring reliable grid operation to cope with more volatile south-north flows, and at increasing the exchange capacities between France & Belgium to sustain an adequate level of market integration. | 2022 | Mid-term Project | ELIA;RTE
France - Germany | Muhlbach - Eichstetten | Operation of a second circuit at 400kV OHL Muhlbach - Eichstetten, instead of the currently operated circuit Eichstetten - Vogelgrun at 225kV. Some restructurations on the existing grid may be necessary in the area. Reinforcement of the existing circuit at 400kV OHL Muhlbach - Eichstetten in order to increase the thermal capacity of the line. | 300 | ​Security of supply (mutual support), Exchange capacity improvement between France and Germany | TYNDP2014 and Common Planning Studies. Reclustering of TYNDP2014 project 152. Both investments of project 152 (Muhlbach - Eichstetten and Vigy - Uchtelfangen) have been studied and assessed in a common study performed by the concerned TSOs in the framework of TYNDP2014 and German National Grid Development Plan | 2025 | Long-term Project | RTE;TransnetBW
France - Germany | Vigy - Uchtelfangen area | ​​Upgrade of existing transmission OHL between Vigy and Uchtelfangen (or beyond) to increase its capacity | 1500 | ​Positive impact on the exchange capacity between France and Germany | TYNDP 2014 and Common Planning Studies. Reclustering of TYNDP2014 project 152​. Both investments of the project 152 (Muhlbach - Eichstetten and Vigy - Uchtelfangen) have been studied and assessed in a common study performed by the concerned TSOs in the framework of TYNDP2014 and German National Grid Development Plan. Details of the technical realisation are currently under investigation. | 2030 | Long-term Project | Amprion;RTE
France - Great Britain | ElecLink | ​​Eleclink is a new FR – UK interconnection cablewith 1000 MW capacity​ though the channel Tunnel between Sellindge (UK) and Mandarins (FR). Converter stations will be located on Eurotunnel concession at Folkestone and Coquelles. This HVDC interconnection is a PCI project (Project of Common Interest) no. 1.7.3. | 1000 | 172 | Following the completion of initial studies which confirmed that the development of an interconnector in the Tunnel is technically possible and economically viable, ElecLink is now completing the development work to bring the project to Financial Close. ElecLink has submitted and received its regulatory exemption from the UK and FR regulators, signed grid connection agreements for access to the national transmission systems in the UK and FR, obtained its electricity interconnector licence in the UK, carried out its public consultation for the project works in the UK, received conditional approvals for the converter stations in the UK and FR, and has invited market participants to register their interest in contracting interconnector capacity.​ | 2018 | Mid-term project | ElecLink
France - Great Britain | France-Alderney-Britain | ​France-Alderney-Britain (FAB) is a new HVDC subsea interconnector between Exeter (UK) and Cotentin Nord (France) with 1,4 GW capacity. The investment has been selected as PCI 1.7.1 in the NSCOG corridor. | 1400 | 153 | The project will not only increase the interconnection between Great Britain and continent but also integrate additional RES (especially RES in Great Britain). 2,8 GW of future tidal generation could also be connected to this link when it develops off the Cotentin Coasts. | 2022 | Mid-term Project | RTE and FABLINK limited
France - Great Britain | IFA2 | ​​​IFA2 is a new HVDC VSC subsea interconnector that will develop​ between Tourbe (area of Caen) in France and the Chilling (region of Southampton) in Great Britain. It has been selected as PCI 1.7.2 in the NSCOG corridor on 14/10/13. | 1000 | 25 | The objective is to increase the interconnection capacity between Great Britain and Continent and to integrate RES generation, especially wind in Great Britain. | 2020 | Mid-term Project | NGT;RTE
France - Great Britain | New Great Britain France interconnector | New HVDC link between France (connection area in Normandy) and Great Britain​ (South East area) | 1000 | RES connection, Market integration | Common Planning Studies​ | 2030 | Future Project | National Grid;RTE
France - Great Britain | AQUIND Interconnector | ​The Project is to develop a high voltage direct current subsea interconnector power transmission cable between the United Kingdom and France with the total capacity of up to 2000MW and other associated installations as explained herein. The interconnector will land and connect to the United Kingdom grid in the South East of England. The connection point in France will be on the Normandy Coast.​ | 2000 | To generate revenues for the energy generator, for traders using the link, and for the owner of the interconnector.To reduce the consumer cost of energy for the nation in receipt of the energy.To potentially reduce the CO2 content in the UK energy mix.To aid in the creation of a single European energy market.To improve security of supply for each of the interconnected networks.To act as a balancing mechanism for networks with a high penetration of intermittent renewable energy sourcesTo provide a sustainable and reliable source of energy import and export for both of the interconnected networks.To support the target of achieving 10% interconnectivity for the GB network, relative to its peak capacity, by 2020. | (tbc) | 2020 | Future project | Aquind Limited
France - Ireland | Celtic Interconnector | ​Celtic Interconnector will be the first interconnection between Ireland and France. This HVDC (VSC) link with 700 MW capacity is presently being surveyed from Cork harbour (Ireland) to La Martyre (Finistère) in France. The project has been selected as PCI 1.6 in the NSOG corridor on 14/10/13 | 700 | 107 | The project will not only create a direct link between the French and Irish markets but also increase RES integration, especially wind in Ireland. it will also allow mutual support between Ireland and Brittany. | 2025 | Long-term Project | EIRGRID;RTE
France - Italy | Italy-France | ​The Project comprises a new HVDC interconnection between France and Italy as well as the removing of limitations on existing 380 kV internal Italian lines. The removing of limitation is necessary to take full advantage of the increase of interconnection capacity provided by the cross-border line. | Direction A: 1200 - Direction B: 1000 | 21 | The project favours the market integration between Italy and France as well as the use of the most efficient generation capacity; it also increases possible mutual support of both countries. In addition, the project can contribute to RES integration in the European interconnected system by improving cross border exchanges. Such benefits are ensured within different future scenario. | 2019 | Mid-term Project | RTE;TERNA
France - Switzerland | Lake Geneva South | ​This project comes on top of "Lake Geneva West" and "upstream grid reinforcement in France" projects. It consists in upgrading to 400-kV the existing 225-kV overhead line south of Lake Geneva. | FR-> CH 400 ; CH -> FR 1000 | 199 | Main benefits are expected in terms of market integration and better integration of Swiss hydro generation, especially storage. | 2026 | Future Project | RTE;SWISSGRID
France - Switzerland | Lake Geneva West | ​The project consists of uprating the existing 225-kV double circuit overhead line Genissiat- (FR) - Verbois (CH) in order to increase its capacity. | FR->CH 500 ; CH->FR 0 | 22 | The project will increase the capacity from France to Switzerland and secure the supply of Geneva. | 2020 | Mid-term Project | RTE;SWISSGRID
France - Switzerland | Upstream reinforcement in France to increase FR-CH capacity | ​The project consists in attracting the flows to the interconnection south of Lake Geneva in order to alleviate the congestion on the link west to Lake Geneva ​​. It is necessary before implementing "lake Geneva South" project but could not be clustered due to the 5-year clustering rule. It consists in a phase-shifter in Cornier substation (FR) together with an uprate of the existing Creys-St Vulbas 400-kV double-circuit OHL to increase its capacity. | FR->CH 1100; CH->FR 500 | Market integration​ also Swiss hydro generation integration, including pump storage | ​The studies followed up those conducted in the framework of TYNDP2014, aiming at better defining the project "lake Geneva South" and its integration in the grid. | 2020 | Future Project | RTE
France - Switzerland | Concept project France-Switzerland 400kV AC | ​The project consists of a new 400-kV cross-border line between France and Switzerland. Although this project is at vey conceptual stage, for the assessment, connections could be considered in Genissiat (FR) and Verbois (CH). | 1000 | ​Market integration,also Swiss hydro generation integration, including pump storage. | Common Planning Studies showed the interest to ​develop the France-Switzerland profile by 2 GW in the Long Term High RES scenario on top of "Lake Geneva West" and "Lake Geneva South" already included in TYNDP2014. This project contributes to this objective. | >2030 | Future Project | RTE;swissgrid
France - Switzerland | Concept project France-Switzerland HVDC | ​This concept project is a new HVDC between France and Switzerland. | 1000 | ​Market integration, also Swiss hydro integration including pump storage. | Common planning Studies showed the interest to develop the France-Switzerland profile by 2 GW in the long term scenario wiht high RES on top on the TYNDP2014 "Lake Geneva West" and "Lake Genevaz South" projects. This project contributesd to this objective.​ | >2030 | Future Project | RTE;swissgrid
Germany - Austria | AT - DE | ​This project reinforces the interconnection capacity between Austria and Germany. The national investments comprised are a precondition to achieve the full benefit of the cross border investments and are vital for the Austrian security of supply (e.g. part of the Austrian 380-kV-Security Ring). It supports the interaction of RES in Northern Europe (mainly in Germany) and in the eastern part of Austria with the pump storages in the Austrian Alps and therewith facilitates their utilisation. | 2900 | 47 |  | 2021 | Mid-term Project | AMPRION;APG;TENNET-DE
Germany - Netherlands | Long-term conceptual interconnector DE-NL | Market analysis revealed the need for additional cross-border capacity between Germany and The Netherlands. Therefore a bilateral study is started to investigate options for a further increase, in addition to existing and planned interconnections, of the cross border capacity Germany and The Netherlands. | 1000 | Market integration leads to high social economic welfare increase in extremely high RES scenario planning studies | ​Common Planning Studies based on TYNDP2014 Vision 4 | >2030 | Future Project | Amprion;TenneT TSO
Germany - Norway | Norway - Germany, NordLink | ​NordLink: a new HVDC connection between Southern Norway and Northern Germany. Estimated subsea cable length: 514km. Capacity: 1400 MW. | 1400 | 37 | A 514 km long subsea interconnector between Norway and Germany is planned to be realized in 2020. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal/wind/solar-based Continental system. The interconnector will improve security of supply both in Norway in dry years and in Germany in periods with negative power balance (low wind, low solar, high demand etc.). Additional the interconnector will be positive both for the European market integration, for facilitating renewable energy and also for preparing for a power system with lower CO2-emission. The interconnector is planned to be a 500 kV 1400 MW HVDC subsea interconnector between southern Norway and northern Germany. | 2020 | Mid-term Project | STATNETT;TENNET-DE
Germany - Sweden | Hansa PowerBridge 1 | HVDC ​​​​cable interconnector between Sweden (SE4) and Germany (50Hertz). There have been joint studies with 4 options for this project. A second connection (Hansa PowerBridge 2) is under investigation. | 700 | 176 | Comment on the RES integration: The project helps integrating wind power on both sides and improves power balancing. Comment on the S1 and S2 indicators: The project will have a social and environmental impact. However, the project is in an early stage and there is not enough facts regarding the impact. | 2024 | Long-term Project | 50HERTZ;SVK
Germany - Austria | Area of Lake Constance | The transmission capacity of the 380-kV-grid in this grid area and especially the cross-border lines between Germany and Austria are extended significantly by this project. Capacity overloads with existing lines are eliminated and therefore connection between the German and the Austrian transportation grid is strengthened. | 1000 | 198 |  | 2023 | Long-term Project | AMPRION;TRANSNET-BW
Germany - Switzerland | Concept project Germany-Switzerland | The project will have a significant relation to the projects Swiss Roof I and Swiss Roof II and therefore will have relation to the border CH-DE. The effect of the border CH-DE has been already considered within the projects Swiss Roof I and Swiss Roof II. | 1000 | ​The TYNDP 2016 Common Planning Studies showed the interest to increase the Germany-Switzerland capacity by 1 GW on top of the 'Swiss Roof I' and 'Swiss Roof II' projects that correspond to the 'Swiss Roof' project of TYNDP 2014. This project contributes to this objective. | ​The TYNDP 2016 Common Planning Studies showed the interest to increase the Germany-Switzerland capacity by 1 GW on top of the 'Swiss Roof I' and 'Swiss Roof II' projects that correspond to the 'Swiss Roof' project of TYNDP 2014. This project contributes to this objective. | >2030 | Future Project | swissgrid;TransnetBW;Amprion
Great Britain - Central Europe | Long-term conceptual "West-East corridor" in North Sea | Potential synergies between interconnectors and internal grid reinforcements, enabling further market integration between Great Britain and Central Europe, is to be further studied within the concept of a "west-east corridor" | TBD | ​Long-term perspective as per the analyzed TYNDP14 Vision 4 scenario induces reflection upon a corridor from Great Britain to Central Europe, with possible multi-terminal take-off points in Benelux, France and Germany | Common Planning Study​ | >2030 | Future Project | Amprion;Creos Luxembourg;Elia System Operator;National Grid;RTE;TenneT TSO
Great Britain - Netherlands | New Great Britain - Netherlands Interconnector | Indentified through RES studies. HVDC link between South East coast of Great Britain and the Netherlands​ | 1000 | RES connection​ integration | Common Planning Studies | 2030 | Future Project | National Grid;TenneT TSO GmbH
Great Britain Norway | Norway-Great Britain NSN | ​NSN, 1400 MW interconnector Norway and England. | 1400 | 110 | A 720 km long subsea interconnector between Norway and England is planned to be realized in 2021. When realized it will be the world's longest. The main driver for the project is to integrate the hydro-based Norwegian system with the thermal/nuclear/wind-based British system. The interconnector will improve security of supply both in Norway in dry years and in Great Britain in periods with negative power balance (low wind, high demand etc.). Additional the interconnector will be positive both for the European market integration, for facilitating renewable energy and also for preparing for a power system with lower CO2-emission. The interconnector is planned to be a 500 kV 1400 MW HVDC subsea interconnector between western Norway and eastern England. | 2021 | Mid-term Project | NGT;STATNETT
Great Britain - Norway | NorthConnect | A 650 km long subsea interconnector between Norway and Scotland is planned to be realized in 2022. The interconnector is planned to be a 500 kV, 1400 MW HVDC subsea interconnector between western Norway (Simadalen) and eastern Scotland (Peterhead), UK. | 1400 | 190 | ​tbc | 2022 | Mid-term project | NorthConnect
Hungary - Slovenia | CSE3 | ​The project consists of a new double circuit 400 kV line Cirkovce-Pince and a new 400 kV Cirkovce substation (Slovenia) by which a new connection to one circuit of the existing double circuit interconnection line between Hungary and Croatia will be made, thus creating two new cross border interconnection between Slovenia and Hungary and between Slovenia and Croatia. Existing 220 kV lines of the corridor Cirkovce-Divaca will be upgraded to 400 kV level. | HU->SI: 1700 - SI->HU: 2000 | 141 |  |  | Mid-term Project | ELES;MAVIR
Hungary-Romania | HU-RO | ​400kV OHL between Hungary and Romania. In Romania a new transformer 400/220kV in Rosiori substation is necessary as internal investment associated to this project. | 500 | ​market integration under high RES conditions | ​Common Planning Studies 2015 performed based on TYNDP2014 Vision 4 | >2030 | Future Project | MAVIR ZRt;Transelectrica
Iceland - Great Britain | Interco Iceland-UK | ​Interconnector (Sea cable) between Iceland and Great Britain. The Cable is DC with 800-1200 MW capacity and over 1.000 km long. 99.98% of the generation in Iceland is RES. Icelands hydro generation is highly flexible and ideal for complementing intermittency of GB’s growing wind sector. | 1000 | 214 |  |  | Future Project | LANDSNET;NGT
inside-DE | OWP Northsea TenneT Part 4 | Connection of offshore wind parks in the North Sea to Germany. Mainly subsea DC cable. The OWP will help to reach the Eropean goal of CO2 reduction and RES integration | 3600 | 129 |  | 2031 | Future Project | TENNET-DE
inside-DE | OWP TenneT Northsea Part 2 | ​Connection of offshore wind parks in the North Sea to Germany. Mainly subsea DC cable. The OWP will help to reach the Eropean goal of CO2 reduction and RES integration | 5400 | 191 |  | 2022 | Mid-term Project | TENNET-DE
inside-DE | OWP Northsea TenneT Part 3 | ​Connection of offshore wind parks in the North Sea to Germany. Mainly subsea DC cable. The OWP will help to reach the Eropean goal of CO2 reduction and RES integration | 4500 | 192 |  | 2027 | Future Project | TENNET-DE
inside-downstream | East Anglia Cluster | This investment is internal to the NGET TSO. This group of investments are in response to an expected growth in offshore wind and nuclear generation in and around the area at stake and is located north and east to London.​ | 3600 | 69 | To facilitate Offshore and nuclear developments | 2023 | Future Project | NGT
inside-inside | Reinforcement Northwestern DE | ​Integration of on- and offshore RES in Lower Saxony | 5500 | 207 |  | 2024 | Long-term Project | 50HERTZ;AMPRION;TENNET-DE
inside-inside | N-S Western DE_section North_1 | ​Integration of on- and offshore RES in Lower Saxony | 5500 | 208 |  |  | Mid-term Project | 50HERTZ;AMPRION;TENNET-DE
inside-inside | Reinforcement Northeastern DE | ​New 380-kV-lines in the area of Schleswig-Holstein mainly for integration of Onshore-Wind. | 12000 | 209 |  |  | Mid-term Project | 50HERTZ;AMPRION;TENNET-DE
inside-inside | N-S transmission DE_par_line_2 | ​new 380-kV-OHL between Thuringa and Bavaria due to increase of RES in Northen Germany | 11800 | 204 |  | 2024 | Long-term Project | 50HERTZ;TENNET-DE
inside-inside | N-S transmission DE_par_line_1 | ​new 380-kV-OHL between Thuringa and Bavaria due to increase of RES in Northern Germany | 11800 | 205 |  | 2015 | Mid-term Project | 50HERTZ;TENNET-DE
inside-inside | N-S Eastern DE_central section | ​North-South transmission in Germany. AC links from Northern Germany towards the load centers of Bavaria and Baden-Württemberg. | 11800 | 164 |  | 2022 | Mid-term Project | AMPRION;TENNET-DE
inside-inside | Reinforcement Southern DE | ​"AC-busbar" in Southern Germany for energy dispatching within Bavaria and Baden-Württemberg and gathering solar energy. | 11800 | 206 |  | 2024 | Long-term Project | TENNET-DE;TRANSNET-BW
inside-outside | RES in north of Portugal | ​This project integrates new amounts of Hydro Power Plants in the Northern region of Portugal and creates better conditions to evacuate Wind Power already existent and new with authorization for connection (with the reinforcement of the local 220kV network). These new amounts of power will increase the flows in the region, and it is expected that the flows could reach 3800 MW, which must be evacuated to the littoral strip and south Portugal through three new 400kV independent routes. Part of these flows will interfere and accumulate with the already existent flows entering in Portugal through the international interconnections with Spain on the North, the 400kV Alto Lindoso-Riba de Ave-Recarei and Lagoaça-Aldeadávila axis, which induces additional needs for reinforcement of this axis in a coordinated way. | Direction A: 3700-5100 - Direction B: 0-0 | 1 |  | 2022 | Mid-term Project | REN
inside-outside | Baza project | A new double circuit Caparacena-Baza-La Ribina 400 kV OHL, in Spain with two new 400 kV substations in Baza and La Ribina. This project will allow integrating an important contingent of wind and solar generation, both at transmission and distribution level in an area of Jaen where the transmission network is very weak. Moreover, a new pumping hydropower plant with pumping storage is expected in this area. On the other hand, the project will help reducing congestion in the existing single circuit Litoral- Tabernas-Hueneja-Caparacena 400 kV, between Almeria and Granada ​ | Direction A: 550-770 - Direction B: 3280-3630 | 13 | RES integration and constraints solution | 2025 | Future Project | REE
inside-outside | Integration of RES in Alentejo | ​This project integrates new amounts of solar (and also some wind) generation in the south of Portugal. The existing network of 150 kV is not sufficient to integrate these amounts of power and a new 400 kV axis should be launched in this region, establishing a connection between the two Southern interconnections between Portugal and Spain, the Ferreira doAlentejo-Alqueva-Brovales andTavira-Puebla deGusman. This axis will also close a ring of 400 kV in the Southern part of Portugal that will guarantee the load growth in the region (Algarve is one of the regions that presents the biggest growth rate in Portugal) in a safe, secure and quality way. | Direction A: 1400 - Direction B: 0 | 85 |  | 2025 | Long-term Project | REN
inside-outside | CSE8 Transbalkan Corridor | ​​ The project aim is to increase transmission capacity within Serbia and facilitate exchange of energy between north-east part of Europe and south-west of Europe. | 300 | 227 |  |  | Mid-term project | EMS
Internal Belgian Backbone East | Internal Belgian Backbone East | ​In a first step (2015) the axis Gramme-Van Eyck is reinforced via the realization of a second 380kV circuit involving the creation of a substation 380 at Van Eyck as well as the installation of a new 380kV circuit in high performance conductors over a distance of about 30km between Van Eyck & Zutendaal. In a latter step (2020-2025) the 'full upgrade' to high-perfomance conductors is envisioned between Gramme & Van Eyck, combined with the installation of a second 380kV circuit between Meerhout & Van Eyck. The need for this latter step is subject to further monitoring of the evolution of the (transit)flux and the potential of new production units that could be deployed within the area. | 1400 | This project englobes the development of the internal backbone at the east side of Belgium to accommodate the potential new production units in the area and to sustain the development of cross-border capacity. | TYNDP14​ - reclustering of project # 24: Belgian North Border | 2020 | Mid-term Project | Elia System Operator
Internal Belgian Backbone West | Internal Belgian Backbone West | Upgrade consists of replacing the current double circuit 380kV conductors between Horta and Mercator with high performance conductors allowing to double the transport capacity of the axis. The line currently passing Mercator going to Doel will be integrated into Mercator substation to obtain a better flux balance and avoid an upgrade between Mercator & Doel at this stage. | 1500 | This project covers the development of the internal backbone at the west side of Belgium, which needs to be upgraded in order to transport higher fluxes between France, Stevin & the Netherlands. Furthermore, the upgrade facilitates connection of possible new generation. | ​TYNDP14 - reclustering of project # 24: Belgian North Border | 2019 | Mid-term Project | Elia System Operator
Internal Belgium | Belgian North Border (BRABO) | Reinforcements are grouped in a modular way into "BRABO" project: - BRABO I (2016): integration of 4th PST on Belgian North Border combined with second 380kV line between Doel & Zandvliet - BRABO II (2020) + BRABO III (2023): realization of a new 380kV AC connection Zandvliet-Lillo-Mercator, including a new 380kV substation at Lillo​ | 1000 | 24 | The need to reinforce the Belgian North Border is driven by a congruation of factors - ensuring reliable grid cooperation in a context of increasing & more volatile international fluxes on Belgian's which could cause internal congestions and negatively effect market capacity - desire to further develop market capacity between Belgium & the Netherlands with +- 1000 MW - possible connection of new central production units - increasing industrial demand around Antwerp harbour area | 2020 | Mid-term Project | ELIA
Internal boundary in France North-South | Massif Central North | ​ ​​The project is a new 400 kV line in an existing corridor. The precise description of the project needs additional studies. | Direction A: 3300 - Direction B: 3800 | 216 | The main driver of the project is the integration of future hydro generation and specially new pump storage. The project is also needed to accomodate some scenarios with high RES and nuclear shutdown. | 2030 | Long-term Project | RTE
Internal boundary in France North-South | Massif Central South | ​ The project will develop in the north-to-south direction in the south of the Massif Central area (France), between Rueyres and La Gaudière. It will mainly consists in a new double-circuit 400-kV overhead line substituting to the existing 400-kV single circuit line. | Direction A: 3300 - Direction B: 3800 | 158 | The main driver for the project is the integration of existing and new wind & hydro generation in the Massif Central (France) including possible pump storage. | 2025 | Long-term Project | RTE
Internal boundary in Germany | HVDC Brunsbüttel/Wilster to Großgartach/Grafenrheinfeld | 4 GW HVDC connection from Northern Germany (areas of Brunsbüttel/Wilster) to Bavaria / Baden-Württemberg (areas of Großgartach/Grafenrheinfeld) | 4000 | ​Integration of RES and security of supply of Southern Germany | NEP (German NDP) | 2022 | Mid-term Project | TenneT TSO;TransnetBW
Internal Boundary in North-East Germany | 380-kV-grid enhancement between Area Güstrow/Bentwisch and Wolmirstedt | ​380-kV-grid enhancement between the areas Güstrow/Bentwisch and Wolmirstedt. | 1500 | This Project will help to transport the expected amount of RES to the South of Germany. It will also help to increase the technical possibility in this area to integrate the expected new Interconnectors to Scandinavia (e.g. Hansa Power Bridge or Kontek 2). | NEP (German NDP) | 2020 | Mid-term Project | 50Hertz Transmission
Internal Boundary in North-East Germany | Offshore Wind Baltic Sea (I) | ​AC grid connections connecting Offshore Wind Farms in Cluster 1 of the Baltic Sea (see German Offshore Grid Development Plan). Cluster 1 is located north east of Rügen in the German Exclusive Economic Zone. | 750 | ​RES connection | ​German Offshore Grid Development Plan | 2018 | Mid-term Project | 50Hertz Transmission
Internal Boundary in North-East Germany | Offshore Wind Baltic Sea (II) | ​AC grid connections connecting Offshore Wind Farms in Cluster 1, 2 or 4 of the Baltic Sea (see German Offshore Grid Development Plan). Clusters are located north east of Rügen mainly in the German Exclusive Economic Zone. | 500 | RES connection | ​German Offshore Grid Development Plan | 2026 | Long-term Project | 50Hertz Transmission
Internal boundary in south-western France | Façade Atlantique | Investments in France. Upgrade of the North-South 400 kV corridor between Aquitaine (Cubnezais) and Vallée de la Loire (Tabarderie). Exact scope of the project will be defined in the follow up of the studies. | 3000 | ​Market integration, RES connection. The projects allows to evacuate to the North of France additional generation located in the South West of France, specially Solar and wind. It is needed for high exchange between France and Spain. | Common Planning studies​. Internal studies performed by RTE. | 2030 | Future Project | RTE
Internal boundary in Spain (generation) | Spanish Pumping | Potential necessary transmission development for the connection of potential 3rd party storage projects (mainly pumping storage) in the TYNDP​ | 3000 | storage connection and evacuation​ | none​ | 2020 | Future Project | REE
Internal boundary in Spain Navarra-Basque Country or ES-FR | Connection Navarra-Basque Country | New OHL 400kV double circuit Ichaso-Castejón/Muruarte 400kV​ | 1500-2000 | Essential project to connect futureFR-ES Navarra-Atlantic Pyrenees, but independently to this, it is required for internal needs such as solve existing congestions between Navarra and Basque Country and RES integration in the area ​ | National Development Plan and Common Planning Studies​ | 2020 | Mid-term Project | REE
Internal Boundary in West-Germany | Ultranet | ​2 GW HVDC-connection from the Region of Osterath (Rhineland) to the Region of Philippsburg (Baden-Württemberg). New circuit on an existing route on the same pylons as AC lines. | 2000 | Integration of RES and security of supply of South-Germany. | NEP (German NDP) | 2019 | Mid-term Project | Amprion;TransnetBW
Ireland - Great Britain | Ireland GB Interconnector | EWIC HVDC interconnector between National Grid and EirGrid​ | 700 | 106 | Connection now connected and operational | 2012 | Mid-term Project | EIRGRID;NGT
Ireland - Northern Ireland | North South Interconnector | A new 400 kV interconnector between Woodland in Ireland and Turleenan in Northern Ireland.​ | 800 | 81 |  | 2019 | Mid-term Project | EIRGRID;SONI
Ireland - Northern Ireland | RIDP I | The infrastructure development is required to facilitate connection of renewable generation in the North and West of the Island. It will further integrate the Ireland and Northern Ireland transmission systems and provide capacity for substantial demand growth in the area.​ | 570 | 82 |  | 2030 | Future Project | EIRGRID;SONI
Italy - Montenegro | Italy-Montenegro | The Italy-Montenegro interconnection project includes a new HVDC subsea cable between Villanova (Italy) and Lastva (Montenegro) and the DC converter stations.The HVDC link between Italy and Balkans is strictly correlated with the Transbalkan Corridor (projects 146 and 227) and the Mid Continental East Corridor (project 144). | 1200 | 28 | The project have a significant cross border impact, because it make possible to increase the use of existing and future interconnections all along the corridor between Italy and Continental East Europe including the Member States Romania and Bulgaria; it helps to use most efficient generation capacity; enables possible mutual support of Italian and Balkan power systems; contributes to RES integration in the European interconnected system by improving cross border exchanges. Such benefits are ensured within different future scenarios. | 2019 | Mid-term Project | CGES;TERNA
Italy - Tunisia | Italy-Tunisia | The project consists in a new interconnection between Tunisia and Sicily to be realized through an HVDC submarine cable. | 600 | 29 | The project favours the use of the most efficient capacity in the PAN European interconnected system. The project also increases the system operational flexibility. Such benefits are ensured according to different future scenarios. | 2030 | Future Project | TERNA
Italy - Switzerland | Greenconnector | ​Greenconnector is an HVDC interconnector project between Italy and Switzerland for power transport using DC cables rather than overhead lines. The route length is about 150 km. The design power is 1000 MW (1200 MW in overload condition), while the DC voltage is +/- 400 kV DC. Two cables will be installed, working with a bipolar scheme. Great part of the cables route will exploit a section of an existing oil pipeline, no longer in service since January 1997. This pipeline crosses the Italian and Switzerland border at Splügenpass and is running close by the two end stations of the Greenconnector project (Sils in Graubunden Canton and Verderio Inferiore, Lecco). The cables will be pulled inside the pipeline itself, reducing the amount of civil works required before and after cable laying and therefore limiting even temporary environmental impact. For about 47 km the cables will run across the Como lake.​ | 1000 | 174 | (tbc) | 2021 | Mid-term project | Worldenergy SA
Italy - Switzerland | Merchant line "Castasegna (CH) - Mese (IT)" | "The planned Transmission project is a merchant line on the swiss-italian border between Castasegna (CH) and Mese (IT). The planned Cable connection in 220 kV AC has a length of around 14 km, 13.5 of witch in Italy. In connection with the realisation of the project a Rationalisation of the 380 and 132 kV Grid in the region Mese (Provincia di Sondrio) is planned. The expected NTC increase is around 200 MW. The main Project elements are (merchant line):220 kV Connection to the Swiss HVG in Castasegna220 kV Cable line of around 14 km between Castasegna and Mese220/380 kV Substation with PST 250 MVA in Mese The Grid Rationalisation in the Region of Mese foresees the following actions:Displacement of 2 km of the 380 kV Line ""Soazza – Bulciago""Realisation of a new 380/132 kV Substation in Mese (Transformation 2 x 250 MVA)Displacement of 0.8 km of 132 kV LinesRealisation of 2.6 km of 132 kV Cable connectionsDemolition of 2.45 km of 380 kV line and 2.3 km of 132 kV lines" | 200 | The project has a relevant impact on the 3 pillars of EU energy policy:Address the market integration increasing the interconnection capacity between CWE and Italy;Improve significantly the sustainability promoting a better dispatching of the existing hydro generation in the region as well as the rationalisation of the existing HV Grid in Mese --> substitution of existing 132 kV overhead transmission line with underground transmission cables and unlock valuable municipal land;Improve the security of system operation removing existing bottlenecks in the north Italian HVG and easing dispatching of local hydro generation. | ​The project is in authorisation process. All preliminary studies have been done. Project Status: design and permittini phase. | 2018 | Mid-term project | Repower
Lithuania - Sweden | NordBalt phase 2 | ​​​​This is second phase of DC interconnector between Lithuania and Sweden that will connect the Baltic grid to the Nordic and integrate the Baltic countries (Estonia, Latvia, Lithuania) with the Nordic electricity market and will also increases security of supply. Second phase includes network reinforcements in Sweden and in Lithuania to be able to fully utilize the interconnector between Lithuania and Sweden.This is PCI project. | 0 | 124 | Internal investments after 2020 in Lithuania and Sweden are needed to be able to fully utilize the 700 MW interconnector between Lithuania and Sweden. Investments include new 330 kV OHL in Lithuania and new 400 kV OHL in Sweden. The project is a key for the SoS of the Baltic states. The project helps integrating RES, especially in the Baltic states but also in the southern Sweden. | 2023 | Long-term Project | AST;LITGRID;SVK
Lithuania - Sweden | NordBalt phase 1 | ​​​​DC interconnector between Lithuania and Sweden and internal investments in Lithuania, Latvia and Sweden. The project will connect the Baltic grid to the Nordic and integrate the Baltic countries with the Nordic electricity market. | 700 | 60 | The investments before 2020. DC interconnector between Lithuania and Sweden and internal investments in Lithuania, Latvia and Sweden. The project will connect the Baltic grid to the Nordic and integrate the Baltic countries with the Nordic electricity market and also increases security of supply. <RES comment>The project helps integrating RES, especially in the Baltic states but also in the southern Sweden. <SoS comment>The project is a key for the SoS of the Baltic states. | 2020 | Mid-term Project | AST;LITGRID;SVK
Luxembourg - Belgium | Luxembourg-Belgium Interco | First a phase-shift transformer is integrated at Schifflange (LU) in order to control the transit flows from Germany to Belgium, hereby enabling the line Aubange (BE) - Schifflange (LU) to figure as interconnector. Furthermore, the Luxembourg network is being reinforced by creating a loop around Luxembourg city, including substations for in feed in lower voltage levels.On a longer-term perspective, the further development of interconnection capacity between Belgium & Luxemburg via two cables between Aubange (BE) & Bascharage (LU) is being studied. | 700 | 40 | The project envisions the realization of an interconnection between Luxembourg and Belgium allowing to increase the transfer capability between LU, DE, BE and FR and contributing to the security of supply of both countries. | 2017 | Future Project | AMPRION;CREOS;ELIA;RTE
Netherlands - Germany | Reinforcements Ring NL | ​ The project reinforces the Dutch grid to accommodate new conventional and renewable generation, to handle new flow patterns and to facilitate the cross-border capacity increase with neighbouring countries. The project investments are spanning overall from 2019 to 2024. Project 168 "Spaak" is closely related to this project, as ithas the same drivers and benefits as project 103 and can be seen as a long term investment of project 103.The two projects have been assessed as a whole and share the same common assessment. | 300 | 103 | Accommodate new conventional and renewable generation, to handle new flow patterns and to facilitate the cross-border capacity increase with neighbouring countries. | 2030 | Long-term Project | TENNET-NL
Netherlands - Germany | Doetinchem - Niederrhein | This new AC 400-kV double circuit overhead line will interconnect The Netherlands and Germany (Ruhr-Rhein area). Upon realization of the project, the border between The Netherlands and Germany will consist of four double circuit interconnections in total. The project will increase the cross border capacity and will facilitate the further integration of the European Energy market especially in Central West Europe. | 1500 | 113 |  | 2017 | Mid-term Project | AMPRION;TENNET-NL
Netherlands - Germany | Spaak NL | Project 168 "​Spaak" associates to project 103 the "Dutch ring"as a second phase long term investment , to be commissioned in 2030. Both projects reinforce the Dutch grid to accommodate new conventional and renewable generation, to handle new flow patterns and to facilitate the cross-border capacity increase with neighbouring countries. The two projects have been assessed as a whole and share the same common assessment. | 250 | 168 | Accommodate new conventional and renewable generation, to handle new flow patterns and to facilitate the cross-border capacity increase with neighbouring countries. | 2025 | Future Project | TENNET-NL
Netherlands - Germany | 201 Upgrade Meeden - Diele | ​Increase of the interconnection capacity between The Netherlands and Germany by approximately 500 MW by adding two new phase shifting transformers and upgrade of an existing 400 kV double circuit tie line between Meeden and Diele. The project will increase the cross border capacity and hence increase the market capacity between the two countries. This will lead to better price convergence in the region. Furthermore the energy from RES sources can better be integrated in the Dutch and German system, avoiding spillage and in extreme cases the increase of the interconnection capacity and controllability helps in securing the system. | 500 | ​Market integration, RES integration, security of supply |  | 2018 | Mid-term project | TenneT TSO;TenneT TSO GmbH
North-South | Godelleta-Morella/La Plana | This projects consist of a new OHL 400 kV AC axis Godelleta-Morella/La Plana (Spain) and represents the reinforcement of the Mediterranean axis needed to accommodate geographical unbalances between North and South, especially between Castellón and Valencia, which besides are influenced by the exchanges with France. Congestions are expected due to important south-north flows caused by renewable energy sources (onshore wind but mainly solar), which result in dumped energy without the project. ​ | Direction A: 670-850 - Direction B: 1400-1500 | 193 | market and RES integration. Constraints solution | 2023 | Future Project | REE
North-South | Black Sea Corridor | ​The project consists of one 400kV double circuit OHL Cernavoda-Stalpu and Gura Ialomitei, one 400 kV double circuit OHL Smardan-Gutinas and one 400 kV OHL single circuit Suceava – Gadalin, in Romania and also the new 400 kV OHL Dobrujda-Burgas in Bulgaria. This project allows transfer of generation from the Western cost of the Black Sea towards consumption and storage centers in Central Europe and South-Eastern Europe. | Direction A: 1260 - Direction B: 2196 | 138 | The project reinforces the internal corridors in Romania and Bulgaria connecting the Black Sea Coast windy are to the rest of Europe, and also increases the cross-border tranfer capacity between Romania and Bulgaria. | 2021 | Mid-term Project | TRANSELECTRICA, ESO-EAD
North-South | CSE4 | ​The project concerns the construction of new AC 400kV overhead lines at the south part of Bulgaria and a new AC 400kV interconnection between Bulgaria and Greece. This project will increase cross border transfer capacity between Bulgaria and Greece and contribute to the safe evacuation of renewable power in the area. | Direction A: 648 - Direction B: 82 | 142 | This project will facilitate market integration by increasing the transfer capacity in the Bulgaria-Greece borders. It will also contribute to increase the volume of exchanges between the Continental Europe synchronous area and Turkey. Furthermore it will contribute to the safe evacuation of the power from the wind farms expected to be installed in the North-East part of Greece and the North-East of Bulgaria as well as photovoltaic power plants in the South part of Bulgaria. Mentioned project will be composed of a new 400kV AC interconnection between Bulgaria and Greece as well as two new 400kV OHL aiming at the strengthening of the transmission network at the South part of Bulgaria. | 2021 | Mid-term Project | ESO;IPTO-SA
North-South | BOG & Stevin | STEVIN extends the 380kV backbone to the coastal area, via the construction of a new +-50km (40km OHL; 10km cable) double-circuit between Zomergem and Zeebrugge, including the construction of a new substation in Zeebrugge and transition stations for the cable-line transitions. BOG considers the eruption of an offshore hub connected to the onshore grid (at Zeebrugge) via AC underground cables, including the necessary reactive compensation for these cables. | Direction A: 3000 - Direction B: 0 | 75 | This project facilitates the integration of up to 2,3 GW of offshore capacity into the Belgian grid via the modular development of an offshore hub (BOG: Belgian Offshore Grid project) and the extension of the 380kV backbone to the coastal area (STEVIN project) The final design as well as the legal, ownership & regulatory framework for BOG is being defined in concertation with the stakeholders (wind farm developers,...). BOG is presented here into the extent that it would be considered as regulated infrastructure. Note that the STEVIN project is also required for the integration of the NEMO interconnector (BE-UK). | 2018 | Mid-term Project | ELIA
North-South | Anglo-Scottish Cluster | These projects facilitate the connection of RES and the connection of the remote Scottish Islands. ​ | 4200 | 77 | These projects facilitate the connection of RES and the connection of the remote Scottish Islands. | 2023 | Future Project | NGT;SHETL
North-South | Offshore Wind Baltic Sea | Grid connections of offshore wind farms (AC), connecting offshore wind farms in the Baltic Sea to the German transmission grid in Bentwisch, Lüdershagen and Lubmin. | 4500 | 46 |  |  | Future Project | 50HERTZ
North-South | CSE9 | ​The project is comprised of investments in Serbia, FYR of Macedonia, Albania and Greece. These investments include new AC 400kV overhead lines and relevant substations. The project will increase transfer capacity in the predominant North-South direction of the CSE Region. | Direction A: 1157 - Direction B: 2709 | 147 | The project aims to increase the transfer capacity in the predominant North-South direction that is from Romania, Serbia and Bulgaria towards Greece, FYR of Macedonia and Albania. In addition, a part of this project will increase the security of supply in the South-West part of the FYR of Macedonia. The investments forming the project are 400 kV lines and corresponding substations located in Greece, FYR of Macedonia, Serbia and Albania. |  | Mid-term Project | EMS;IPTO-SA;MEPSO
Italy South - Italy Center | Central Southern Italy | ​The project consists in the reinforcement of southern Italy 400 kV network through new 400 kV lines as well as upgrading of existing assets. The activities will involve the network portions between the substation of Villanova and Foggia, Deliceto and Bisaccia as well as Laino and Altomonte. | Direction A: 0 - Direction B: 1000 | 127 | The projects allows removing internal bottlenecks and increases market and RES integration. | 2019 | Mid-term Project | TERNA
Italy Center- Italy South | Central Northern Italy | ​The project consists in the strengthening of interconnection between the northern and the central part of Italy. It will involve the upgrading of existing 220 kV over-head line to 400 kV between Colunga and Calenzano substations as well as the removing of limitations on the existing 220 kV network in Central Italy. | 600 | 33 | The projects allows removing internal bottlenecks and increases market and RES integration. | 2020 | Mid-term Project | TERNA
North-South | HVDC Wolmirstedt to area Gundremmingen | 2 GW HVDC-connection from Wolmirstedt to the area of Gundremmingen. Capacity extension to 4 GW is under investigation. | 2000 | 130 |  |  | Mid-term Project | 50HERTZ;AMPRION
North-South | Longterm German RES | ​internal German DC-Link for RES integration | 18000 | 133 | This project becomes necessary in case of further long-term strong increase in RES generation like in Vision 3 and 4. The project is not in Vision 1 and 2. It connects areas with high installed capacities of RES and areas with high consumption and storage capabilities. For this reason the development of new North-South and Northeast- Southwest electricity transmission capacity in Germany is necessary. This project begins in the North and North-East of Germany, areas with high RES generation (planned and existing) and connections with Scandinavia (planed and existing).The project ends in the South of Germany, an area with high consumptions and connections to Austria and Switzerland (transit to Italy and pump storage in the Alps). | 2034 | Future Project | 50HERTZ;AMPRION;TENNET-DE;TRANSNET-BW
North-South | N-S Western DE_parallel lines | Grid reinforcement between North-West-Germany and South-West-Germany to integrate RES. | 5500 | 135 | RES integration and system stability. | 2022 | Mid-term Project | AMPRION
North-South | N-S Western DE_section North_2 | ​New 380-kV-OHL and one DC-Link in North-West Germany for integration of RES, mainly on- and offshore wind. | 5500 | 132 |  | 2022 | Mid-term Project | AMPRION;TENNET-DE
North-South | N-S Western DE_section South | North-South transmission Western Germany - AC reinforcements and upgrades towards the load centers of Baden-Württemberg and Switzerland | 5500 | 134 | RES integration and system stability | 2021 | Mid-term Project | AMPRION;TRANSNET-BW
North-South | OWP TenneT Northsea part 1 | ​Connection of offshore wind parks in the North Sea to Germany. Mainly subsea DC cable. The OWP will help to reach the Eropean goal of CO2 reduction and RES integration | 5750 | 42 |  | 2017 | Mid-term Project | TENNET-DE
North-South | SE North-south reinforcements | Sweden internal line. ​Overhead line 400 kV. ​Reinforcements, both lines and stations, in and between bidding area SE1, SE2 and SE3 will accomplish RES integration in northern Sweden. | 700 | 126 | Comment on the RES integration: the project will help integrating 700-800 MW of RES in northern Sweden and Norway. Comment on the S1 and S2 indicators: the project will have a social and environmental impact but the investments are in early stages so there are no facts regarding the impact. | 2025 | Long-term Project | SVK
outside-inside | Asturian Ring | This project consist of closing the 400kV Asturias Ring in the northern part of Spain, and comprises a new 400 kV OHL line between Gozón and Sama, with two new 400kV substations in Reboria and Costa Verde (Spain) , which main purpose is support the distribution network. Therefore, this project is required to ensure the security of supply in the area of Asturias in a future with very low thermal generation in the region. ​ | Direction A: 400-500 - Direction B: 700-700 | 151 | Security of supply | 2026 | Future Project | REE
outside-inside | east of Austria | ​To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") the transmission grid infrastructure (currently a rather weak 220kV line) has to be enforced and new substations for the connection need to be erected. | 1500 | 186 | To allow the grid integration of the planned renewable energy generation (mainly wind power) in the north-eastern part of Austria ("Weinviertel") and to cover the foreseen load growth in that region the transmission grid infrastructure has to be enforced and new substations for the connection need to be erected | 2021 | Mid-term Project | APG
outside-inside | 2nd Offshore-Onshore Corridor (Belgium) | To evacuate up to 3.3 GW wind, thus 1 GW more than currently planned, preliminary studies indicated that this corridor could consists of a 1 GW DC connection from an offshore platform or nearby Stevin substation in Zeebrugge towards the Antwerp Area (substation Doel could be a possible location) Additional solutions are needed on top op the 1 GW connection to the Antwerp area to integrate the full potential of 4 GW offshore wind. This could take the form of a complementary connection towards Izegem or Brussels, as well as a larger dimensioning of the connection to the Antwerp area. The determination of optimal location/route, technology and the integration of this corridor in relation to an eventual offshore hub/grid are subject of further studies. | 1700 | 120 | This is a conceptual project that could be considered as a long-term investment option, triggered by high-RES scenarios where up to 4GW of offshore capacity is envisioned in the Belgian part of the North Sea (note that this 4 GW is not ensured in official government plans). Compared to the current forecast of 2,3 GW of offshore capacity as to which Elia's portfolio is designed, it implies an additional reinforcement under the form a second offshore-onshore corridor. Preliminary analysis indicates that this corridor could consist of multiple reinforcements to different inland locations. | 2030 | Future Project | ELIA
Poland - Germany | GerPol Improvements | Upgrade of the existing 220 kV double interconnection line between Krajnik and Vierraden to 400 kV double line in the same direction together with installation of Phase Shifting Transformers on two existing interconnection lines (Krajnik-Vierraden by 50Hertz Transmission GmbH in Vierraden and Mikułowa-Hagenverder by PSE S.A. in Mikułowa) on the PL/DE border including an upgrade of substations Vierraden, Krajnik and Mikułowa | Direction A: 0-1500 - Direction B: 0-500 | 94 | This Project contribute to the following: • decreasing of unscheduled flow from Germany to Poland, Poland to Czech Republic and Poland to Slovakia by increasing of controllability on entire synchronous profile; • enhancement of market capacity on Polish synchronous profile - PL/DE as well as PL-CZ/SK border in case of both import and export. The project provides additional capacity (NTC – Net TransferCapability) of 500 MW in terms of import and 1500 MW export; greater level of safety and reliability of operation of the transmission network in Poland due to enhanced control of power flow. | 2017 | Mid-term Project | 50HERTZ;PSE
Poland - Germany | GerPol Power Bridge I | ​The reinforcements in the Polish transmission network in western part of the country near Polish/German border : construction new AC 2x400 kV lines Mikułowa - Świebodzice, Krajnik - Baczyna and Baczyna - Plewiska. | 1500/500 | Project contributes to the following:• increase of market integration between member states - additional NTC of 1500 import and 500 MW export on PL-DE/SK/CZ synchronous profile; • integration of additional Renewable Energy Sources on the area of western and north-western Poland as well as eastern part of Germany; • improving network security - project contributes to increase of security of supply and flexibility of the transmission network (security of supply of Poznań agglomeration area). | ​TYNDP 2014, Common Planning Studies | 2022 | Mid-term Project | 50Hertz Transmission;PSE
Poland - Germany | GerPol Power Bridge II | ​Project consist from following investments: indentation to the 2x400 kV line Baczyna-Plewiska (new routes: Baczyna-Zielona Góra, Zielona Góra-Plewiska), 2x400 kV line Zielona Góra - Gubin, crossborder line 2x400 kV line Gubin (PL)-Eisenhuettenstadt (DE), new station Zielona Góra, new station Gubin (with Phase Shifting Transformers). | 1500 | The project contributes to the following:-increase of market integration between member states - additional NTC of 1500 MWimport on PL-DE/SK/CZ synchronous profile; -integration of additional Renewable Energy Sources on the area of western and north-western Poland as well as eastern part of Germany. | TYNDP 2014​ | 2030 | Future Project | 50Hertz Transmission;PSE
Poland - Lithuania | LitPol Link Stage 2 | ​The LitPol Link Stage 2 is a continuation of building of the interconnection between Poland and Lithuania in order to achieve the planned transmission capacity of 1000 MW in both directions. Building of additional internal investments in Poland and Lithuania are necessary.This is PCI project. | 500-1000 | 123 | The project improves connection the Baltic States to the Continental Europe and Baltic Sea ring. The analysis shows that the project improve Security of Supply, increase ability integrating RES and avoided spillage in Baltic States and Poland. | 2020 | Mid-term Project | LITGRID;PSE
Portugal - Spain | Interconnection Portugal-Spain | A new OHL 400kV interconnection betweenFontefría ( Spain) and Ponte de Lima (Portugal). Internal reinforcements complement the cross border section, such as the axis in Spain betweenFontefría andBeariz and in Portugal between Ponte de Lima (previouslyViana do Castelo), Vila Nova deFamalicão (previously Vila doConde) and Vermoim/Recarei. This project was included in the 2013 PCI list (PCI 2.17). | ES->PT 1900 MW and PT->ES 1000 MW | 4 | This project will allow to increase the interconnection capacity between Portugal and Spain up to governmental agreements. Larger and more volatile flows are expected between both countries due to the huge increase of volatile sources and the market interchanges. The project includes a new 400kV interconnection route in the North (Fontefría-Ponte de Lima), besides the 400kV internal reinforcements required, due to the important loop flows between the two countries. This project will also have a benefit in reducing the spilled energy in the Iberian Peninsula. | 2018 | Mid-term Project | REE;REN
Romania - Serbia | Upgrading existing single 400 kV interconnection line between Romania and Serbia to double 400 kV line | Upgrading existing single 400 kV interconnection line between Romania and Serbia to double 400 kV line | 500 | ​Market integration under high RES conditions | The project necessity stems for the need to increase the target transfer capacity between RS and RO in order to accommodate connection of RES and improve market integration, according to the results by the Common Planning Studies based on TYNDP2014 Vision 4.​ | >2030 | Future Project | JP EMS;Transelectrica
Serbia internal | Network upgrade in Central Serbia from 220 kV to 400 kV voltage level | ​This project is linked with the new double 400 kV tie line between Bulgaria and Serbia project which is the outcome from Common Planning Studies during making RegIP2015. This project will increase transmission capacity in the East - West corridor (from Bulgaria and Turkey to West Balkan and Italy). With realization of this project an internal botlenecks in RS will be resolved which will have direct impact on increasing BTC values on the following borders: BG-RS, ME-RS and BA-RS. | 500 | Market integration​ |  | 2030 | Long-term Project | JP EMS
Serbia internal | Closing of 400 kV ring around Belgrade region | ​This project will close the 400 kV ring around region of Belgrade. The project will increase transmission capability in the direction EAST - WEST and increase reliability of supply of Belgrade city. With realization of this project an internal bottlenecks in RS will be resolved which will have direct impact on increasing BTC values on the border RO-RS. | 500 | ​Market integration and Security of Supply | Common planning studies and internal network studies | 2030 | Long-term Project | JP EMS
Slovakia - Hungary | New SK-HU intercon. - phase 1 | This project will increase the transfer capacity between Slovak and Hungarian transmission systems, improve security and reliability of operation both transmission systems and support North - South RES power flows in CCE region. Main investments of this project are double circuit AC OHL 400 kV from new Gabcikovo (Slovakia) substation to Gönyű (Hungary) substation and double circuit AC OHL (preliminary armed only with one circuit) 400 kV from Rimavska Sobota (Slovakia) substation to Sajóivánka (Hungary) substation. | Direction A: 0-500 - Direction B: 0-425 | 48 | This project will increase the transfer capacity between Slovak and Hungarian transmission systems, improve security and reliability of operation both transmission systems and support North - South RES power flows in CCE region. Main investments of this project are double circuit 400 kV line from new Gabcikovo (Slovakia) substation to Gönyű (Hungary) substation and double circuit 400 kV line from Rimavska Sobota (Slovakia) substation to Sajóivánka (Hungary) substation. The project supports the North - South power flow from wind and photovoltaic power in Northern part of Continental Europe by increasing GTC of SK-HU profile and improves the possibilities of balancing the system. The project enhances system security of both Slovak and Hungarian system, especially during outages and maintenances on other interconnections between the countries. | 2018 | Mid-term Project | MAVIR;SEPS
Slovakia - Hungary | New SK-HU intercon. - phase 2 | This project will increase the transfer capacity between Slovak and Hungarian transmission systems, improve security and reliability of operation both transmission systems and support North - South RES power flows in CCE region. Realization of this project is tightly connected to the negotiations between Slovak and Ukrainian TSOs regarding future operation of the existing Slovak interconnection with Ukraine. Main and only investment of this project is double circuit AC OHL 400 kV from Velke Kapusany (Slovakia) substation to Kisvárda region (Hungary). | 0-500 | 54 | This project will increase the transfer capacity between Slovak and Hungarian transmission systems, improve security and reliability of operation both transmission systems and support North - South RES power flows in CCE region. Realization of this projetct is tightly connected to the negotiations between Slovak and Ukrainian TSOs regarding future operation of the existing Slovak interconnection with Ukraine. Main and only investment of this project is double circuit AC OHL 400 kV from Velke Kapusany (Slovakia) substation to Kisvárda region (Hungary). The project supports the North - South power flow from wind and photovoltaic power in Northern part of Continental Europe by increasing GTC of SK-HU profile and improves the possibilities of balancing the system. The project enhances system security of both Slovak and Hungarian system, especially during outages and maintenances on other interconnections between the countries. | 2029 | Long-term Project | MAVIR;SEPS
Slovenia - Italy | Italy-Slovenia | ​The project consists in a new HVDC link between Salgareda (Italy) and Divača\Beričevo (Slovenia) which will strengthen the connection between Slovenia and Italy. | Direction A: 800 - Direction B: 700 | 150 | The project increases the transmission capacity between Slovenia and Italy and allows stronger market integration between Italy and Slovenia and broader region. Such benefits are ensured according to different future scenarios. The project could also improve the reliability and security of supply by allowing mutual support of both countries. | 2022 | Mid-term Project | TERNA;ELES
Sicily - Italy South | Sicily-Mainland | The project consists in the strengthening of Sicily - mainland 400 kV interconnection through a new double circuit line which will be realized partly as a subsea cable as well as over-head line.The activity is part of the wider network reinforcement program which involves the Sicilian 400 kV grid. | 1000 | 30 | The project allows removing internal bottlenecks and increases market and RES integration. The expected commissioning date is 2015 therefore afterwards it will be dropped from TYNDP 2016 | 2015 | Mid-term Project | TERNA
South-North | Cartuja | The 400 kV double circuit Cartuja-Arcos de la Frontera and the Cartuja 400 kV substation intend to be the connection point of an important amount of wind power energy in the coastal area of Cadiz, mainly offshore but also onshore. In case of low wind production, the project will be useful as an additional injection for secure the load in the area of Cadiz. ​ | Direction A: 425-600 - Direction B: 1560-2700 | 194 | RES integration, and SoS | 2029 | Future Project | REE
Spain - France | Biscay Gulf | The project is a subsea HVDC link (2000 MW) between Gatica (Basque Counrty, ES) and Cubnezais (Aquitaine, FR), that came up as the preferential strategy after deep technical and environmental prefeasibility studies ​​accross the whole French-Spanish border. | Direction A: 2600 - Direction B: 2200 | 16 | The project is necessary to achieve the political will to increase the connection of the Iberian Penisula to the European market. Its location allows to balance the flows on the Western and Eastern axes of the border, optimising the use of existing grid and avoiding any internal reinforcement. TYNDP2014 studies showed it would bring significant Socio-economic welfare by allowing the use of cheaper and more efficient technologies and avoiding RES spillage, especially in the Iberian Peninsula. | 2022 | Mid-term Project | REE;RTE
Spain - France | PST Arkale | This project is a new PST (phase shifting transformer) in the Spanish substation Arkale 220 kV with affection to the Arkale-Argia cross border line between France and Spain. This device is required to increase the France-Spain exchange capacity, especially from Spain to France, and not only is able to have an independent good impact in the exchange capacity without taking into account the Eastern and Western interconnections, but also helps making the most of these projects. In addition, as this project avoids the tripping of the Arkale-Argia tie line in case of contingencies, it helps improving the Security of supply in the French Basque country. This project have been included in the 2013 PCI list ​ | Es->FR: 500MW - FR->ES: 100MW | 184 | market integration, increase of crossborder capacity ES-FR | 2017 | Mid-term Project | REE
Spain - France | Additional project France - Spain | Additional projects for the 10% ratio in case of. The projects have to take into account all the 3rd Party projects. | 1500 | ​Market integration | ​TYNDP 2016 | 2030 | Future Project | RTE;REE
Spain - France | FR-ES project -Navarra-Landes | A new interconnection between France and Spain in the Western part of the Pyrenees between Dicastillo (Spain) and Cantegrit (France). The project is considered as a HVDC project of 2x1000 MW. Internal reinforcements complement the cross border section, such as the upgrade of the connections of Cantegrit with Saucats and Marsillón, and the connection of the new Dicastillo substation. ​ | 1500-2000 | Market Integration. Increase capacity in the French-Spanish border. Increase of the Interconnection ratio for Spain and the Iberian Peninsula as political guidelines.​ | Common Planning Studies, eHighway2050​ | 2023 | Long-term Project | REE;RTE
Spain - France | FR-ES project -Aragón-Atlantic Pyrenees | A new interconnection between France and Spain in the Central part of the Pyrenees between Sabiñánigo (Spain) and Marsillón (France). Internal reinforcements complement the cross border section, such as a new 400 kV line between Sabiñánigo and Cinco Villas, including both substations. | 1500-2000 | Market Integration. Increase capacity in the French-Spanish border. Increase of the Interconnection ratio for Spain and the Iberian Peninsula as political guidelines.​ | Common Planning Studies, EHighway2050​ | 2023 | Long-term Project | REE;RTE
Spain - Portugal | Uprate the western 220kV Sevilla Ring | Uprate the 220 kV lines D.Rodrigo-Aljarafe and Aljarafe-Santiponce to increase their capacity​ | ​500 PT-->ES | Market integration in the Spanish-Portuguese border. Some congestions in the transmission network of Sevilla decrease in certain demand/generation situations the cross border exchange capacity in order to maintain the security of the network and fulfill the network codes. | TSO and bilateral planning Studies in the short term.​ | 2019 | Mid-term Project | REE
Spain - Portugal | Douro Spanish-Portuguese reinforcement | Reinforcement of the Douro cross border region pending for complementary studies for a better definition of the investments. Draft proposal is the reinforcement of the axis Armamar (PT) - Pocinho (PT) ‑ Lagoaça (PT) ‑ Aldeadávila (ES) ‑ Villarino (ES) | PT->ES 700MW; ES->PT 300MW | ​Market Integration in the Spanish-Portuguese border, by eliminating cross border congestions in a high RES future scenario | ​TYNDP 2016Common Planning Studies | 2030 | Future Project | REE;REN
Sweden (SE4)-Germany | Hansa PowerBridge 2 | Possible second HVDC cable interconnector between southern Sweden (Bidding area SE4) and Germany (50Hertz). This project candidate is motivated by market based target capacities found in the Common Planning Studies by Regional Group Baltic Sea. | 700 | ​Market integration, RES integration and Security of supply | Common Planning Studies for TYNDP 2016.​ Possible additional internal reinforcements are not included in project cost | 2025-2030 | Future Project | 50Hertz Transmission;Svenska Kraftnät
Switzerland | Swiss Ellipse I | ​The project helps accommodate new pump storage units which mainly support the increasing RES generation in the European areas with solar and wind generation. | 3350 | ​Market integration, RES connection | re-clustering of TYNDP2014 project 91 | 2022 | Mid-term Project | swissgrid
Switzerland | Swiss Ellipse II | ​The project helps accommodate new pumping storage units which mainly support the increasing RES generation in the European areas with solar and wind generation. | 1650 | ​Market integration, RES connection | re-clustering of TYNDP2014 project 91 | 2029 | Long-term Project | swissgrid
Switzerland - Germany; and Switzerland - Austria | Swiss Roof I | ​This project increases the capacity between CH and its neighbours DE and AT. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. | DE > CH: 1700 MW AT > CH: 500 MW CH > DE: 700 MW CH > AT: 500 MW | ​Market Integration, Security of Supply, RES connection | re-clustering of TYNDP2014 project 90 | 2022 | Mid-term Project | swissgrid
Switzerland - Germany; and Switzerland - Austria | Swiss Roof II | ​This project increases the capacity between CH and its neighbours DE and AT. This enables to connect large renewable generation in Northern Europe to pump storage devices in the Alps, thus noticeably increasing the mutual balancing between both regions. | DE > CH: 1700 MW AT > CH: 500 MW CH > DE: 700 MW CH > AT: 500 MW | ​Market Integration, Security of Supply, RES connection | re-clustering of TYNDP2014 project 90 | 2022 | Future Project | swissgrid
Switzerland - Italy | Italy-Switzerland | ​The project consists of a new 400 kV line San Giacomo-Pallanzeno, conversion from AC to DC of the 220 kV line, including the realization of the 2 AC/DC converter stations and 220 kV to 400 KV substation upgrade. Additional internal lines in Italy and in Switzerland are required to get full advantage from the interconnection capacity provided by the cross-border line. | Direction A: 1000 - Direction B: 950 | 31 | The project significantly increases interconnection capacity between Switzerland and Italy; favours the market integration; helps to use of the most efficient generation capacity and could potentially contribute to RES integration. Such benefits are assured according to different future scenarios. | 2022 | Mid-term Project | SWISSGRID;TERNA
UK - Ireland | Irish Scottish Links on Energy Study (ISLES) | ​ISLES consists of a coordinated offshore grid in the Irish sea and west of Scotland, providing market-to-market interconnection and connection to renewable generation functionalities. The concept ISLES 'zones' consist of a number of complementary multi-terminal HVDC connections that can be operated without the need for DC breakers and without breaching existing onshore loss of in feed limits but which can be reconfigured post-fault to re-establish power transfer paths. The benefits of the design would be that offshore wind or tidal power can be brought to either of two shores, there would be reduced redundancy in connections and, in particular, interconnection capacity would be provided between the GB market and the Single Electricity Market on the island of Ireland. Thus while not 'dedicated to security of supply', realising the ISLES vision would make a significant contribution towards it. Two 'Zones' have been identified:Northern ISLES Corridor (PCI 1.9.2)Southern ISLES Corridor (PCI 1.9.3)" | 1000 | 189 | The project partners secured additional INTERREG IVA funding for a second phase of ISLES in 2013. Entitled ‘Towards Implementation’ it includes three distinct work-streams: ISLES Spatial Plan Network Regulation and Market Alignment Study Business Plan Consultants have been procured to deliver these work-streams and the outputs will begin to emerge May 2015, after a period of extensive stakeholder consultation and engagement. The outputs and recommendations will be disseminated via a number of channels including publications on our website, stakeholder events and final conference events in the summer of 2015. | 2020-2030 | Future Project | the Department of Enterprise, Trade and Investment in Northern Ireland, the Department of Communications, Energy and Natural Resources in Ireland, and the Scottish Government
upstream-downstream | RES in center of Portugal | ​This project integrates new hydro power plants (some of them with pumping) and evacuates the existent and new wind generation in the inner central region of Portugal (the wind target in this region overcomes surmounts of more than 2000 MW). The existing network of 220 kV and 150kV is no more adequate to integrate these new amounts of power, and a new 400kV axis should be launched in this region in two major routes: one to the littoral strip (Penela/Paraimo/Batalha) and another by the interior, establishing a connection to Falagueira substation, where there is an interconnection with Spain (Falagueira-Cedillo). | Direction A: 1200-1600 - Direction B: 0-0 | 2 |  | 2020 | Mid-term Project | REN
West-East | CSE1 | The project will contribute in strengthen Croatian transmission grid along its main north-south axis (in parallel with eastern Adriatic coast) allowing for additional long-distance power transfers (including cross border) from existing and new planned power plants (RES/wind/ and conventional/hydro and thermal/) in Croatia (coastal parts) and BiH to major consumption areas in Italy (through Slovenia) and north Croatia. The increased transfer capacity will support market integration (particularly between Croatia and Bosnia-Herzegovina) by improving security of supply (also for emergency situations), achieving higher diversity of supply&generation sources and routes, increasing resilience and flexibility of the transmission network.​​​ | Direction A: 612 - Direction B: 594 | 136 |  | 2022 | Mid-term Project | HEP;NOS-BIH
West-East | Aragón-Castellón | This project represents the reinforcement of the Cantabric-Mediterranean axis needed to accommodate geographical unbalances between Northern Spain and the Mediterranean area, which otherwise would produce congestions in the 400 kV corridors. Therefore, this project is required to solve constraints in the existing and future network, caused by existing and new RES and because of flows in both directions between Aragón and Castellón, and affected by high exchanges with France. The project consists of two 400kV axis Mudejar-Morella and Mezquita-Morella that converge in an axis Morella-La Plana. The project also includes a new 400kV substation Mudejar with connection to the axis Aragón-Teruel (Spain). ​ | Direction A: 100-900 - Direction B: 1900-2600 | 203 | market and RES integration. Constraints solution | 2016 | Mid-term Project | REE
West-East | South West Cluster | Project needed for renewables off of the South West peninsula, the replanting of Hinkley Point nuclear power station and further CCGT at Seabank. ​ | 3200 | 78 | Project needed for renewables off of the South West peninsula, the replanting of Hinkley Point nuclear power station and further CCGT at Seabank. | 2022 | Future Project | NGT
West-East | Wales Cluster | Reinforcement of the internal grid to facilitate the integration of nuclear plant and RES. ​ | 2000 | 79 | Reinforcement of the internal grid to facilitate the integration of nuclear plant and RES. | 2024 | Future Project | NGT
West-East | CZ West-East corridor | ​The project consists of reinforcements of three 400 kV AC overhead internal lines located in the nothern-western part of the Czech Republic in the west-eastern direction of power flows between existing 400 kV substations Vyskov, Cechy Sterd, Babylon and Bezdecin. The individual reinforcement of the above lines will be achieved by changing the existing single-circuit line to double-circuit line with transmission capacity of 2x1730 MVA. | Direction A: 1250-1750 - Direction B: 1400-1600 | 55 | The project will facilitate power evacuation from the existing and new generation capacities (CCGT and lignite) which are located in the high concentrated power generation capacities in the northern-western part of the Czech grid in the west-eastern direction of the power flow. Moreover the project will prevent the non-fulfilment of operational security criteria of the Czech power system; substantially increase the interoperability and flexibility of the system in the Czech Republic in the norther-western part of the CZ system and ensure the security of supply in all those regions whose supply depend on those lines including the central part where the Capital city is located. Enhancement of the market flows in the norther-western direction is another positive contribution of the project | 2019 | Mid-term Project | CEPS
Inside Germany | Westcoast line | New 380-kV-line Brunsbüttel – Niebül inside Schleswig – Holstein. Main focus of the project is the integration of onshore-RES – mainly wind – in Western Schleswig-Holstein. The project is labeled as PCI 1.3.2. It is the southbound connection of PCI 1.3.1. and is necessary to increase the GTC between Dänemark/West and Germany by 500 MW. | 3000 |  |  | 2018 | Mid-term Project | Tennet-DE
Inside Germany | Audorf-Dollern | New 380-kV-line Audorf – Hamburg/Nord – Dollern” in existing 220-kV-corridor. Main focus of the project is the integration of onshore-RES – mainly wind – in Schleswig-Holstein. The project is labeled as PCI 1.4.2. and 1.4.2. It is the southbound connection of PCI 1.4.1. and is necessary to increase the GTC between Dänemark/West and Germany by 720/1000 MW. | 3000 |  |  | 2017 | Mid-term Project | Tennet-DE

## TYNDP2016 storage
Project candidate name | Country | Type of storage | Maximum active power [MW] | Minimum active power | Maximum reactive power | Minimum reactive power | Connection point to the transmission infrastructure | Voltage at the connection point | Detailed about connection point | Motivation for the project | Status | Total storage capacity [GWh] - and defined as total energy delivered to the grid when reservoir is totally emptied, starting at reservoir full condition | Expected commissioning date
Kruonis pumped storage power plant extension | Lithuania | Pure hydro pumping | 225 | 10.8 | 2020 | [6 empty] | 10.8 | 2020
Hydro Pump Storage Power Plant Pfaffenboden in Molln | Austria | Hydro Pump Storage | 300 | 1.8 | 2019 | [6 empty] | 1.8 | 2019
Reversible pumped-storage hydro-electric exploitation "MONT-NEGRE" power 3300 MW Zaragoza, Spain | Spain | Pure pumping | 3300 | 7511 | 2020 | [6 empty] | 7511 | 2020
Pumped Storage Complex with two independent upper reservoirs: Agios Georgios & Pyrgos | Greece | Hydro (pumped storage) | 594 | 3436 | 2021 | [6 empty] | 3436 | 2021
Battery storage in South Italy | Italy | Battery Energy Storage System (BESS) | 250 | 1.7 | 2022 | [6 empty] | 1.7 | 2022
Muuga HPSPP | Estonia | hydro pump storage | 500 | 6000 | 2023 | [6 empty] | 6000 | 2023
PCI hydro-pumped storage in Bulgaria - Yadenitsa | Bulgaria | Pumped Storage Hydro Power Plant | 864 | 5.2 | 2021 | [6 empty] | 5.2 | 2021
Cruachan II | UK - Scotland | Pump Storage | 600 | 7.2 | 2025 | [6 empty] | 7.2 | 2025
Purifying -Pumped Hydroelectric Energy Storage (P-PHES Navaleo) | Spain | Pure pumping plant | 541 | 3.5 | 2018 | [6 empty] | 3.5 | 2018
Kaunertal Extension Project | Austria | Pumped Hydro Storage | 1076 | 152 | 2028 | [6 empty] | 152 | 2028
MAREX storage | Ireland | PHES pure pumping | 1500 | 6 | 2020 | [6 empty] | 6 | 2020
iLand | Belgium | Pumped Hydro - Offshore | 550 | 2 | 2021 | [6 empty] | 2 | 2021
CAES Larne, Northern Ireland | Northern Ireland | Compressed air energy storage | 330 | 2 | 2020 | [6 empty] | 2 | 2020
Coire Glas | UK | Hydro Pumped Storage | 600 | 30 | 2023 | [6 empty] | 30 | 2023

## Reference capacities
Reference Capacities covering present situation, mid-term and long-Term projects but not including future projects [MW]
Border | 2020 Expected Progress | 2030 Visions
AL-MK | 200 | 200
AL-RS | 760 | 760
AT-CH | 1700 | 1700
AT-CZ | 1000 | 1000
AT-DE | 5000 | 7500
AT-HU | 1200 | 1200
AT-IT | 555 | 1655
AT-SI | 1200 | 1200
BA-HR | 1344 | 1844
BA-ME | 500 | 500
BA-RS | 1100 | 1100
BE-DE | 1000 | 1000
BE-FR | 2800 | 2800
BE-GB | 1000 | 1000
BE-LUB | 380 | 380
BE-LUG | 700 | 700
BE-NL | 2400 | 2400
BG-GR | 1728 | 1728
BG-MK | 530 | 530
BG-RO | 1400 | 1400
BG-RS | 600 | 600
CH-AT | 1700 | 1700
CH-DE | 4700 | 6100
CH-FR | 1300 | 1300
CH-IT | 6240 | 6240
CY-GR | 2000 | 2000
CZ-AT | 1200 | 1200
CZ-DE | 2100 | 2600
CZ-PLE | 0 | 0
CZ-PLI | 500 | 500
CZ-SK | 2100 | 2100
DE-AT | 5000 | 7500
DE-BE | 1000 | 1000
DE-CH | 3286 | 6686
DE-CZ | 1500 | 2000
DE-DKE | 1000 | 1000
DE-DKW | 3000 | 3000
DE-FR | 3000 | 4800
DE-LUG | 2300 | 2300
DE-NL | 4450 | 5000
DE-NO | 1400 | 1400
DE-PLE | 0 | 0
DE-PLI | 2000 | 2000
DE-SE | 615 | 1315
DKE-DE | 1000 | 1000
DKE-DKW | 600 | 600
DKE-PL | 0 | 0
DKE-SE | 1700 | 1700
DKW-DE | 3000 | 3000
DKW-DKE | 600 | 600
DKW-GB | 1400 | 1400
DKW-NL | 700 | 700
DKW-NO | 1640 | 1640
DKW-SE | 740 | 740
EE-FI | 1016 | 1016
EE-LV | 1600 | 1600
ES-FR | 5000 | 8000
ES-FR-GB | 0 | 0
ES-PT | 4200 | 4200
FI-EE | 1000 | 1000
FI-NO | 0 | 0
FI-SE | 2300 | 2800
FR-BE | 4300 | 4300
FR-CH | 3700 | 3700
FR-DE | 3000 | 4800
FR-ES | 5000 | 8000
FR-GB | 5400 | 5400
FR-IE | 0 | 700
FR-IT | 4350 | 4350
FR-LUF | 380 | 380
GB-BE | 1000 | 1000
GB-DKW | 1400 | 1400
GB-FR | 5400 | 5400
GB-FR-ES | 0 | 0
GB-IE | 500 | 500
GB-IS | 0 | 0
GB-NI | 500 | 500
GB-NL | 1000 | 1000
GB-NO | 1400 | 1400
GR-BG | 1032 | 1032
GR-CY | 2000 | 2000
GR-IT | 500 | 500
GR-MK | 350 | 350
HR-BA | 1312 | 1812
HR-HU | 2000 | 2000
HR-IT | 0 | 0
HR-RS | 600 | 600
HR-SI | 2000 | 2000
HU-AT | 800 | 800
HU-HR | 2000 | 2000
HU-RO | 1300 | 1300
HU-RS | 600 | 600
HU-SI | 1700 | 1700
HU-SK | 2000 | 2000
IE-FR | 0 | 700
IE-GB | 500 | 500
IE-NI | 1100 | 1100
IS-GB | 0 | 0
IT-AT | 385 | 1385
IT-CH | 3860 | 3860
IT-FR | 2160 | 2160
IT-GR | 500 | 500
IT-HR | 0 | 0
IT-ME | 1200 | 1200
IT-SI | 1380 | 1380
IT-TN | 0 | 0
LT-LV | 1500 | 2100
LT-PL | 1000 | 1000
LT-SE | 700 | 700
LUB-BE | 0 | 0
LUF-FR | 0 | 0
LUG-BE | 700 | 700
LUG-DE | 2300 | 2300
LV-EE | 1600 | 1600
LV-LT | 1200 | 1800
ME-BA | 400 | 400
ME-IT | 1200 | 1200
ME-RS | 1000 | 1000
MK-AL | 200 | 200
MK-BG | 150 | 150
MK-GR | 400 | 400
MK-RS | 1050 | 1050
NI-GB | 80 | 500
NI-IE | 1100 | 1100
NL-BE | 2400 | 2400
NL-DE | 4450 | 5000
NL-DKW | 700 | 700
NL-GB | 1000 | 1000
NL-NO | 700 | 700
NO-DE | 1400 | 1400
NO-DKW | 1640 | 1640
NO-FI | 0 | 0
NO-GB | 1400 | 1400
NO-NL | 700 | 700
NO-SE | 3695 | 3695
PL-DKE | 0 | 0
PLE-CZ | 600 | 600
PLE-DE | 3000 | 3000
PLE-PL | 0 | 0
PLE-SK | 990 | 990
PLI-CZ | 0 | 0
PLI-DE | 0 | 0
PLI-PL | 2000 | 2000
PLI-SK | 0 | 0
PL-LT | 1000 | 1000
PL-PLE | 3000 | 3000
PL-PLI | 0 | 0
PL-SE | 600 | 600
PT-ES | 3500 | 3500
RO-BG | 1500 | 1500
RO-HU | 1400 | 1400
RO-RS | 1450 | 1450
RS-AL | 330 | 330
RS-BA | 1200 | 1200
RS-BG | 350 | 350
RS-HR | 600 | 600
RS-HU | 600 | 600
RS-ME | 1100 | 1100
RS-MK | 950 | 950
RS-RO | 1050 | 1050
SE-DE | 615 | 1315
SE-DKE | 1300 | 1300
SE-DKW | 680 | 680
SE-FI | 2400 | 3200
SE-LT | 700 | 700
SE-NO | 3995 | 3995
SE-PL | 600 | 600
SI-AT | 1200 | 1200
SI-HR | 2000 | 2000
SI-HU | 2000 | 2000
SI-IT | 1530 | 1530
SK-CZ | 1100 | 1100
SK-HU | 2000 | 2000
SK-PLE | 0 | 0
SK-PLI | 990 | 990
TN-IT | 0 | 0

## Applications incomplete
Transmission projects
Boundary | Project candidate name | Description | Provisional GTC [MW] | TYNDP2014 reference (if applicable) or motivation for new project candidates | Detailed studies | Expected Commissioning Year | Classification | Project promoter(s) | Comment on the non-acceptance of the project
Spain - France - United Kingdom | ANAI: Abengoa Northern Atlantic Interconnection | ​​ANAI project is a new interconnection line proposed by Inabensa (Abengoa). ANAI project will connect Spain - France - United Kingdom with a subsea multiterminal (with Voltage Source Converters) High Voltage Direct Current cable with 2,000 Megawatt of power grid transfer capability. | 2000 |  | (tbc) | 2024/2026 | Future Project | Abengoa | Missing documentation - depending on the country impacted: no formal request for a (pre-)feasibility study has been done or the feasability study provided by the promoter to the TSO has not been approved in its current status.
Spain - France - Italy | ASEI: Abengoa Southern Europe Interconnection | ​​ASEI project is a new interconecnnection line developed by Inabensa (Abengoa). ASEI will connect Spain - France - Italy with a subsea HVDC VSC technology with 2GW power grid transfer capability. | 2000 |  | (tbc) | 2023/2025 | Future Project | Abengoa | Missing documentation - depending on the country impacted: the request for a feasibility study provided is less than 6 months from closure of application window, or the feasability study provided by the promoter to the TSO has not been approved in its current status.
Tunisia, Italia | TuNur | ​TuNur is aimed to connect to the European network a Concentrated Solar Power plant with storage to be located in Rejim Maatoug, Kebili, Tunisia. The connection point to the ENTSO-E network is located in Montalto di Castro, Lazio, Italy. The transmission project will comprise +/- 500kV DC submarine cables from the Tunisian Northern coast to Montalto di Castro, DC overhead lines in Tunisia from the power plant to the shoring point, and HVDC converter stations at the terminal points. | 2000 |  | (tbc) | 30/12/2020 | Future Project | TuNur Ltd | Missing documentation - no agreement between the Tunisian and the Italian ministeries provided.
Greece, Egypt, Libya | LEG1 | ​​​​​ LEG1 is a new project of VDC Interconnection Subsea 3000 MW connecting Egypt to Crete in Greece, via Tobruk in Libya. LEG1 project links European Network and South-East Medring. Following networks can then be linked to Europe: ELTAM, GCC power grid interconnection and EIJLLPST Eight Country interconnection projects. Renewable electricity produced in Libya, Egypt and Saudi-Arabia will be sent to Europe, whilst Europe will help southern countries to face high electricity demand. The HVDC submarine cable can find a path not deeper than 2500m. LEG1 will then challenge the European cable industries in their advanced technology capability.​ | 3000 |  | (tbc) | 2021 | Future Project | GreenPower 2020 | Further clarifications necessary on the request for pre-feasability study made to ADMIE.
UK, France | GridLink | ​UK - France 1.5GW HVDC (VSC) Interconnector | 1500 |  | (tbc) | Q4 2020/ Q1 2021 | Future Project | Elan Energy Ltd | Missing documention- still need to be provided the signed agreement with one of the impacted TSOs.
Ireland - Wales UK | Greenlink | ​​An interconnector link between Ireland and Wales. Using subsea and onshore underground cables. Connecting EirGrid and National Grid networks / systems. Utilising high voltage direct current subsea and onshore cable. | 700 |  | (tbc) | 2020 | Future Project | Element Power | Missing documentation to proof it matches former TYNDP2014 project
Ireland and Great Britain | Greenwire South | ​​Interconnection between Ireland and Great Britain with the option of wind directly connected to Great Britain system, plus system to system (Ireland to Great Britain) interconnection. Using underground and subsea cables. Connecting EirGrid; and/or AC networks in Ireland for directly connected wind; to National Grid. Utilising high voltage direct current (HVDC) and high voltage AC underground cables. | 1300 |  | (tbc) | 2021 | Future Project | Element Power | Missing documentation to proof it matches former TYNDP2014 project
Tunisia, Italia | ITALY - TUNISIA INTERCONNECTION | ​Italy - Tunisia interconnection is a third party cross-border electrical line promoted by Enel Produzione SpA. The project concerns a 500kV d.c. merchant line, 600 MW from Partanna substation (IT) to El Hawaria substation (TN), including 2 converter station AC - DC, one for each side.The electrical interconnection will consist in a monopole undersea cable of about 200 km with a MV return cable and about 20km of underground cable ​​ | 600 |  | (tbc) | 2020 | Future Project | Enel Produzione S.p.A. | Missing documentation - no evidence of an agreement between the Tunisian and the Italian ministeries for this specific project.
UK-Ireland | MAREX UK-Ireland Intrconnector | ​1500MW VSC bipole HVDC interconnector linking UKNG and EIRGRID, submarine Connah's Quay UK to Dublin, OHL/underground cable/submarine cable/OHL Dublin-Bellacorick EIRGRID | 1500 |  | (tbc) | 2020 | Future Project | Organic Power Ltd. | Missing documentation - no evidence provided of a (pre-)feasability study request made to Eirgrid 6 months prior the submission of this project.
Ireland and Great Britain | Greenwire North | ​Interconnection between Ireland and Great Britain with the option of wind directly connected to Great Britain system and system to system (Ireland to Great Britain) interconnection. Using underground and subsea cables.Connecting EirGrid; and/or AC networks in Ireland for directly connected wind; to National Grid. Utilising high voltage direct current (HVDC) and high voltage AC underground cables.​ | 1000 |  | (tbc) | 2021 | Future Project | Element Power | Missing documentation to proof it matches former TYNDP2014 project
North and South Wales | Greenwire Loop | ​A link between Greenwire North converter station and Greenwire South converter station in the Republic of Ireland creates the opportunity for loop flows from North to South Wales - e.g. Pentir to Pembroke and vice versa. The link willl be underground cable, technology and voltage depends on Greenwire south and north designs. | 700 |  | (tbc) | 2022 | Future Project | Element Power | Missing documentation to proof it matches former TYNDP2014 project
Ireland - North Wales UK | Greenconnect | ​​An interconnector link between Ireland and Wales.Using subsea and onshore underground cables.Connecting EirGrid and National Grid networks / systems utilising high voltage direct current subsea and onshore cable.​ | 700 |  | (tbc) | 2022 | Future Project | Element Power | Missing documentation- the request for a feasibility study provided is less than 6 months from closure of application window, so a different criteria must be met
Greece | Southern Aegean Interconnector | ​The project refers to the construction of a submarine DC transmission link to connect the licensed RES plants (mentioned above) at the South Aegean Sea to mainland Greece and the islands of Crete, Kos and the Dodecanese. The capacity of the link will be 600-800MW both directions using HVDC (High Voltage Direct Current) technology. VSA conversion technology in conjunction with plastic (XLPE) cables will be used. The licensed RES projects consist of wind and solar power plants located on 23 small uninhabited islands. The link will be used for transmitting electricity from the RES plants mentioned above to the mainland and the island of Crete. More specifically, the power produced in each island will be transferred to the island of Levitha where the main conversion station will be built acting as a hub. These connections will be AC submarine cables (150 kV or 220 kV). The main link will be an HVDC link connecting the island of Levitha to both the metropolitan area of Athens and the island of Crete; the 400kV substation at Lavrion area will be the connection point in the Athens area and Korakia will be the connection point in Crete (located in the north coast). Both links will consist of two parallel cables in order to increase the reliability of each link; two converter stations are foreseen in Levitha and relevant converter stations in Lavrion and Korakia. Illustrative routing of the links is shown in the attached Entso-e map. The connection to Crete gives further possibilities for power transmission to Cyprus and further to Israel through the "EuroAsia Interconnector" (already accepted as a PCI by the E.C.). It is also possible to further extend this link to the main islands of the Dodecanese complex (namely Kos, Leros, Kalymnos, Nisyros, Tilos) in order to allow the supply of these islands and at the same time the supply of a complex of other smaller islands already connected to the main ones. This is a short link (10km to 15km long) and more likely it will be an AC one. All the installations on the islands (converter stations, substations etc) will be of closed type using GIS technology.​ | 600 | 220 | (tbc) | 2020 | Future Project | Kykladika Meltemia SA | Missing documentation - the promoter did not deliver evidences that the project meet the technical criteria about GTC (the promoter claims a 600 MW increase between CY and GR, but no technical evidence provided).
Shetland - Norway | Maali | ​​An interconnector link between Shetland Scotland UK and Norway. Using subsea and onshore underground cables. Connecting Statnett and National Grid networks / systems. Utilising high voltage direct current subsea and onshore cable. ​ | 600 |  | (tbc) | 2023 | Future Project | Element Power | Missing documentation- the request for a feasibility study provided is less than 6 months from closure of application window, so a different criteria must be met
Northern Ireland – Scotland | Gallant | ​​​​An interconnector link between South West Scotland and Northern Ireland. Using subsea and onshore underground cables. Connecting Northern Ireland Electricity/SONI and Scottish Power / National Grid networks / systems. Utilising high voltage direct current technology. | 500 |  | (tbc) | 2021 | Future Project | Element Power | Missing documentation- the request for a feasibility study provided is less than 6 months from closure of application window, so a different criteria must be met
Spain, France, United Kingdom | Britib | ​Interconnection project between South-West England (United Kingdom), Cordemais (France) and Basque Country (Spain) in a multiterminal HVDC configuration of 525-600 kV with 3 inputs/outputs of 2400 MW each, and a mostly subsea route from Spain to Great Britain along the French coast of about 1330 km in total. | 2400 | A project with a capacity of 1 GW was included in the TYNDP 2014 - project 182 | (tbc) | 2020 | Future Project | ACS Cobra | Missing documentation to proof it matches former TYNDP2014 project
Storage projects
Country | Project candidate name | Type of storage | Maximum active power [MW] | Total storage capacity [GWh] - and defined as total energy delivered to the grid when reservoir is totally emptied, starting at reservoir full condition | Expected commissioning date | Comment on the non-acceptance of the project
Great Britain | CARES (Compressed Air Renewable Energy Storage) | Adiabatic CAES (Compressed Air Energy Storage) | 520 | 6 | 2017 | Missing documentation- the request for a feasibility study provided is less than 6 months from closure of application window, so a different criteria must be met
France | SunHydrO | Distributed Pure Pumped Hydro Storage, both reservoirs being out of river flows (artificial reservoirs) | 12 | 72 | 2020 | Does not meet criteria of connecting to at least 110kV
Spain | ASSS: Abengoa Southern Spain Storage | Battery | 225 | 835 | 2019 | Missing documentation- the request for a feasibility study provided is less than 6 months from closure of application window, so a different criteria must be met
Spain | ANSS: Abengoa Northern Spain Storage | Battery | 225 | 835 | 2019 | Missing documentation- the request for a feasibility study provided is less than 6 months from closure of application window, so a different criteria must be met
Germany | ANGS: Abengoa Northern Germany Storage | Molten salt | 363 | 1059 | 2019 | Missing documentation- no request for feasibility study, signed agreement for study or connection agreement provided
Spain | TWO REVERSIBLE HIDROELECTRIC PLANTS: GIRONES & RAIMATS IN SPAIN | Pure Pumping | 3070 | 24.562 | 2024 | Missing documentation- no request for feasibility study, signed agreement for study or connection agreement provided
Great Britain | CAES Cheshire, UK | Compressed air energy storage | 268 | 1.608 | 2022 | Missing documentation- feasibility study awaiting signing
The Netherlands | CAES Zuidwending, NL | Compressed air energy storage | 330 | 2.64 | 2021 | Missing documentation- no request for feasibility study, signed agreement for study or connection agreement provided
Spain | GIBREX STORAGE | PHES pure pumping | 1500 | 10 | 2022 | Missing documentation- no request for feasibility study, signed agreement for study or connection agreement provided, in addition to missing technical details
Ireland and Northern Ireland | Donegal Storage Project | Hydro Pump Storage | 1500 | 120 | 2022 | Missing documentation- feasibility study given but not performed or acknowledged by TSO